22-State High Voltage Protection Process

Description and Benefits

• High Voltage Protection Equipment (HVPE) serves Network services (permanent or temporary) that are extended into a high voltage environment (e.g., electric power generating, switching, and distribution locations).

• HVPE is required whenever hazardous voltages can appear on those facilities due to GPR (Ground Potential Rise) and/or induction caused by faults in the customer's electrical power system.

• The Power Station HVPE is designed to provide high voltage isolation while enabling telecommunications transmission and signaling over normal telephone pairs.

NOTE**Installation of HPVE is part of the pre-ordering process and HVPE must be paid for before CLEC can proceed to ordering.  CLEC must advise AT&T how it intends to provision the HPVE.  CLEC does this by completing and submitting a form 1039A.  AT&T will review the form and advise CLEC of the cost for the work involved to establish the HPVE.  CLEC must pay this cost before proceeding to ordering its circuits.

Options - How HVPE Works

• The HVPE protects telecommunication equipment where the GPR (Ground Potential Rise) can create hazardous operating conditions.

• HVPE has no conducting paths between terminals on the Central Office side and those on the station side (remote).

• The newer HVPE currently in use is modular and offers easy expansion or change if circuitry application changes.

AT&T has established the following classes and types of HVPE Service Performance Objectives to permit

the customer to specify the HVPE performance objectives for the service provided to power stations:

° Type 1 involves interruptible service performance for AC and DC transmission, which must function during

and after the power fault condition – For Exchange or Private Line Service.

° Type 2 involves non-interruptible service performance for AC and DC transmission, which must function

before, during and after the power fault condition – For pilot wire relaying with DC Supervision.

° Type 3 involves non-interruptible service performance for AC transmission only, which must function before,

during and after the power fault condition – For telemetering or supervisory control circuits.

° Type 4 involves non-interruptible service performance for AC transmission only, only which must function

before, during and after the power fault condition – For audio tone relaying.

Classes:

° Class A HVPE devices up to 2,500 volt, steady voltage.

° Class B HVPE devices up to 4,000 volt, steady state voltage.

° Class C HVPE devices up to 8,000 volt, steady state voltage.

° Class D HVPE devices up to 9,000 volt, steady state voltage.

Pre-Order Procedures for AT&T provided HVPE (ATTHVPE)

1. If the site is a power generating substation or transmission tower, then it is likely the High Voltage Protection Equipment (HVPE) will be required. Customers at these kinds of locations are required to identify these potentially hazardous locations. The following questions can assist in determining if HVPE is required:

• Does this customer location generate or distribute electrical power that is used off-site?

• Does this customer location have any electrical equipment or facilities, such as poles or towers, with high voltage (i.e., equipment with over 150 kilovolts phase to phase)?

NOTE:

Sites with generators or solar panels etc., where the power generated is consumed at the location at voltages less than 150 kilovolts, are not considered high voltage sites.

If this is the first time a location will potentially have HVPE or it is an existing high voltage site that is adding or changing service or the customer is making changes at the location that will impact the existing HVPE configuration, a separate Form ATT 1039A must be prepared. “Request for Services at High Voltage Sites”, per location (i.e., 911 service address) involved. In all regions the ATT1039A form should be completed and e-mailed to the designated mailbox for each region.

| Ordering Region | eMail Address |
| --- | --- |
| East | ATTEastNon-LSRRequest@att.com |
| Midwest | ATTMWNon-LSRRequest@att.com |
| Southwest | ATTSWNon-LSRRequest@att.com |
| West | ATTWestNon-LSRRequest@att.com |
| Southeast | CRSGUNE@att.com |

**LSRs cannot be submitted until all OSPE work is complete and confirmation of work complete is received by the CLEC. When the LSR is submitted a note should be placed in the remarks section designating that the address is HVPE.

NOTE:

Power companies and customers who request services at Power Generator Substations & Towers (PGST) do not always provide accurate information concerning HVPE needs at a location. If the AT&T Engineering team determines that a location is HV and was not accurately identified to AT&T, the CLEC will be instructed to provide accurate information to their LSC representative and that their service request will be delayed until corrected.

HVPE Components

High Voltage Protection Equipment components include:

• Transformers and Neutralizers provided by AT&T

° Copper Solution (Positron and SNC)

° Fiber Solution (RLH and Positron)

° Fuse Link Application (Cable Protection)

• Transformers and Neutralizers provided by the customer

° All customer provided HVPE must be approved prior to installation and inspected after installation by the AT&T ICEP Engineer.

HVPE Dues Date

Dues dates for placing HVPE at power-company / customer locations will be determined after the on-site visit.

***NOTE: For customers with 25 or more locations needing HVPE a project manager will need to be requested.