PHYSICAL COLLOCATION

ENGINEERING

Engineering

General

AT&T will allow the Collocator’s placement of telecommunication equipment for the purposes of interconnecting with AT&T's Network and obtaining access to AT&T's Unbundled Network Elements (UNEs).

AT&T does not assume any responsibility for the design, engineering, testing, or performance of the Collocator's equipment and facilities. However, the Collocator's equipment must meet the same safety criteria and protection standards as does the equipment AT&T utilizes and installs. The Collocator will be expected to conform to the same accepted procedures and standards utilized by AT&T and its contractors when engineering and installing any equipment. The Collocator should refer to CLEC Online web site  https://clec.att.com/clec/  Appendix Section for a list of AT&T standard documents.

AT&T Installation Requirements Guide, Technical Publication (TP76300) contains information which provides Collocators and AT&T approved suppliers, eligible for the scope of work,  with the general requirements affecting building facilities and their care, the installation of central office equipment and the related service requirements to be met prior to, during and following installation activity.

The Collocator is solely responsible for servicing, supplying, repairing, installing and maintaining the following within its Dedicated Space:

- the Collocator’s fiber optic cable(s) or other permitted transmission media to the Dedicated Space;

- the Collocator's equipment including any AT&T provided interconnect equipment provided at the request of the Collocator;

- Collocator's required point of termination cross connects in the Dedicated Space or the optional POT Frame/Cabinet located in the Common Area; and

- POT frame maintenance, including replacement of power fuses and circuit breaker restoration, to the extent that such fuses and circuit breakers are within the CLEC's Dedicated Space or in the optional POT Frame/Cabinet located in the Common Area and accessible by the Collocator and only if required; and the Collocator's connection cable and associated equipment, which may be required within the Dedicated Space(s) or in the optional POT Frame/Cabinet, located in the Common Area to the point(s) of termination.

AT&T neither accepts nor assumes any responsibility whatsoever in any of the areas so designated in this Paragraph below

AT&T will no longer require an Interconnection Bay (i.e. Point of Termination (POT) bay) for physical collocation. The Collocator may furnish and install interconnect panels or blocks within the Collocator's dedicated space "or footprint". Dependent on applicable tariff or Interconnection Collocation Agreement (ICA), the Collocator may elect to have AT&T engineer, furnish and install AT&T standard POT bay/cabinet and interconnect panels. Refer to CLEC Online web site, https://clec.att.com/clec/ Appendix section for AT&T's standard equipment specifications.

.

Types of Equipment That May Be Physically Collocated

"Equipment" means hardware that must use power, have electronics, and provide a Telecommunications Service. The equipment must be a complete piece, unit, or item of such equipment, not a piece-part or sub-component (such as a line card) of a complete unit of equipment. The Collocator may not collocate its equipment sub-components or piece-parts.

Eligible Equipment for Collocation

In accordance with the FCC's In the Matter of Deployment of Wireline Services Offering Advanced Telecommunications Capability: Fourth Report and Order, CC Docket No. 98-147 (Rel. August 8, 2001) during such time period as that order is in effect and reserving all AT&T's rights, AT&T will permit the collocation and use of Equipment pursuant to the standards set forth in this Section and in AT&T's Equipment safety and engineering standards that are set forth in TP76200.

AT&T will allow Equipment to be collocated only under certain conditions:

- if it is "necessary" for interconnection to the AT&T's network for the transmission and routing of telephone exchange service or exchange access or

- for access to AT&T's unbundled network elements ("UNEs") (for the provision of a Telecommunications Service under all the standards and requirements addressed in this Section) or

- when AT&T voluntarily decides to allow the Equipment to be collocated on a non-discriminatory basis

For purposes of this Section, Equipment is considered "necessary" as follows:

- Equipment is considered necessary for interconnection if an inability to deploy that Equipment would (as a practical, economic, or operational matter) preclude the Collocator from obtaining interconnection with AT&T at a level equal in quality to that which AT&T obtains within its own network, or to that which  AT&T  provides to any Affiliate, subsidiary, or other party.

- Equipment is considered necessary for access to a UNE if an inability to deploy that Equipment would, as a practical, economic, or operational matter, preclude Collocator from obtaining nondiscriminatory access to that UNE, including any of its features, functions, or capabilities.

Subject to the requirements of this Section, "Stand-alone Function" Equipment that may be collocated include:

- Transmission equipment that is either optical terminating equipment or a multiplexer

- Equipment being collocated to terminate basic transmission facilities pursuant to sections 64.1401 and 64.1402 of 47 C.F.R. (Expanded Interconnection) as of August 1, 1996.

- Equipment specified in the definition of "Advanced Services Equipment" in section 1.3.d of the SBC/Ameritech Merger Conditions. "Advanced Services Equipment" is defined as, and limited to, the following equipment.

- DSLAMs or functionally equivalent equipment; spectrum splitters that are used solely in the provision of Advanced Services; packet switches and multiplexers such as ATMs and Frame Relay engines used to provide Advanced Services; modems used in the provision of packetized data; and DACS frames used only in the provision of Advanced Services.

- Optical Concentrator Devices ("OCDs") or functionally equivalent Equipment used to provide Advanced Services.

- Remote switch modules ("RSMs") used in conjunction, via an umbilical, with host switches located in different CLEC locations.

AT&T may, at its option and on a non-discriminatory basis, deny collocation of any of the above, or any other Equipment, if collocation of that Equipment would burden AT&T's property interests and if alternative Equipment not imposing such a burden is practically, economically, and operationally available to obtain interconnection or access to UNEs consistent with sections 251(c)(2) and 251(c)(3) of the Act. For AT&T to consider whether a request avoids such burden, the CLEC must provide all information needed by AT&T concerning the equipment or facilities in question, including without limitation its size (height, width, and depth) and its requirements for power, heat, ventilation, air conditioning, and other resources.

In addition, in order for AT&T to determine whether or not Equipment meets the "necessary" standard, CLEC must provide information establishing how it intends to use the equipment for interconnection with AT&T's network for the transmission and routing of telephone exchange service and exchange access and/or for access to AT&T's UNEs for the provision of a telecommunications service. For this purpose, CLEC must identify what it intends to interconnect the Equipment to, and/or what it intends to use the Equipment to access, and must identify the services it intends to use the Equipment to provide.

To qualify for collocation, any of the above Equipment that is used for switching or routing must be (1) "necessary" under the standards set forth above for access to a AT&T UNE sub-loop and must be (2) used solely for that purpose unless it also meets the requirements set forth below for collocating "Multi-functional Equipment."

Equipment excluded from collocation in any other sub-section of this Section also would be excluded as "stand-alone function" Equipment. AT&T will make determinations on a request-by-request basis of whether or not Equipment meets these standards in order to be permitted, or whether or not Equipment will be voluntarily permitted.

Moreover, if CLEC seeks to collocate a switch, CLEC must provide information establishing whether the switch is a packet switch, a circuit switch, or a combination. If the switch is a circuit switch or a combination, CLEC must provide information establishing whether or not the switch is used in conjunction, via an umbilical, with host switches located in different CLEC locations.

AT&T will not allow collocation of, among other Equipment, traditional, circuit switches or enhanced/information services Equipment. For purposes of this section, "traditional, circuit switch" is defined as any Equipment that performs circuit switching independently of other switches or switching systems and does not meet the requirements set forth below for collocating "Multi-functional Equipment." "Traditional circuit switches" include, but are not limited to, the following examples of equipment when such equipment does not meet such requirements: (1) equipment with circuit switching capabilities included in 47 CFR section 51.319(c) which defines "local circuit switching capability" and "local tandem switching capability;" (2) equipment that is used to obtain circuit switching capabilities, without reliance upon a host switch; and (3) equipment with the functionality of a class 4 or 5 switch including, without limitation, the following: Lucent Pathstar, 5E, 4E, or 1A switch; DMS 10, 100, 200, or 250 switch; Ericsson AXE-10 switch; and Siemens EWSD. For purposes of this Section, "enhanced services" are defined as in 47 CFR section 64.702, and "information services" are defined as in section 3(2) of the Act.

For purposes of this Section, "Multi-functional Equipment" is defined as Equipment that combines one or more functions that are necessary for interconnection or access to UNEs with one or more functions that would not meet that standard as stand-alone functions ("Unnecessary Functions"). AT&T will permit the collocation of Multi-functional Equipment if and only if the primary purpose and function of the Equipment, as the Collocator seeks to deploy it, meets all the requirements set forth in Section above for either interconnection or access to UNEs. For a piece of Multi-functional Equipment to be utilized primarily to obtain equal in quality interconnection or nondiscriminatory access to one or more UNEs, there also must be a logical nexus between the additional functions the Equipment would perform and the telecommunication services which the Collocator seeks to provide to its customers by means of the interconnection or UNE. The additional functions must aid in the actual transmission or routing of telephone exchange service and exchange access used with interconnection, or in the actual provision of the telecommunications service used with access to UNEs, in the manner that the CLEC intends to provide such services. For example, AT&T will not allow collocation of certain Equipment including, without limitation, Equipment used to provide payroll processing, data collection, billing, or Equipment that generates customer orders, manages trouble tickets or inventory, or stores customer records in centralized databases, or other operation support systems, or other Equipment that does not provide telecommunications services. Collocator may not collocate Multi-Functional Equipment that has Unnecessary Functions, which significantly increases the burden on AT&T's property interests. For example, the additional functions must not require configuration of the outer boundaries of the CLEC's collocation space, increased floor support, or upgrades to power, air conditioning, heating, or similar plant. AT&T also will consider other potential burdens on a request-by request basis, together with making determinations of whether or not particular Equipment meets all the standards in this section. For AT&T to make these considerations, the CLEC must provide, without limitation, the information described in this section.

Ancillary Equipment or facilities do not provide telecommunications services and are not "necessary" for interconnection or access to unbundled network elements. AT&T voluntarily allows the Collocator to place in its Physical Collocation space certain ancillary Equipment or facilities solely to support and be used with Equipment that the Collocator has legitimately collocated in the same premises. Solely for this purpose, cross-connect and other simple frames, portable test equipment, equipment racks and bays, and potential other ancillary equipment or facilities may be placed in AT&T's premises, on a non-discriminatory basis, only if AT&T agrees to such placement.

Collocator may not collocate certain equipment or facilities which duplicate equipment or facilities used, and functions performed, by AT&T as part of its provision of infrastructure systems for collocation. Such equipment or facilities include, without limitation, Battery Distribution Fuse Bays, air conditioners, heaters, or bulk power plants. These and other types of equipment or facilities that do not provide Telecommunications Services may not be collocated.

AT&T will consider other equipment that provides a Telecommunications Service on a request-by request basis, together with making determinations of whether or not particular Equipment meets all the standards in this Section.

The Collocator will identify the type and quantity of equipment (by manufacturer) that it plans to install in its collocated space. This information will be furnished as part of the "Physical Collocation Application" under the equipment section: "Equipment to be Installed or Removed by Applicant". The "Physical Collocation Application“ is included in Appendix section of the CLEC Online web site. The information will be used by AT&T engineering and architecture personnel to review the equipment to obtain the actual DC current drain, physical data (height, depth, weight, minimum front and rear aisle dimensions, heat release (TP76400), etc.) and floor space requirements. All Collocator’s equipment must meet the Level 1 safety requirements as outlined in AT&T Local Exchange Companies Document, TP76200. The Collocator should provide the information specified in the “Collocator’s Guide to TP76200 Product Evaluation” which may be found in Appendix section of the CLEC Online web site. The Collocation Service Center (CSC) will perform an initial review of the CLEC's proposed equipment and may request that the Collocator to submit a "CLEC Equipment Review Request Form" when additional information is required for AT&T to complete the review of the Collocator's equipment. This form can be found in the Appendix section of the CLEC Online web site https://clec.att.com/clec/ .

Types of Available Physical Collocation Arrangements

AT&T will make each of the arrangements outlined below available within its Eligible Structures in accordance with the Collocation Agreement so that Collocators will have a variety of collocation options from which to choose:

### Caged Physical Collocation

The caged collocation option provides the Collocator with an individual enclosure (not including a top). This enclosure is an area designated by AT&T within an Eligible Structure to be used by the Collocator for the sole purpose of installing, maintaining and operating the Collocator-provided equipment.

Shared Caged Physical Collocation

AT&T will make available shared collocation cages when two (2) or more Collocators submitting simultaneous applications to AT&T. In these instances, AT&T will prorate the charge for site and preparation undertaken to construct the shared collocation cage based upon the percentage of total space utilized by each Collocator. The combined total of the space requested by each Collocator sharing a cage must equal the total square footage of the cage. AT&T will not place unreasonable restrictions on a Collocator's use of a cage, and as such will allow a Collocator to contract with other Collocators to share the cage in a sublease-type arrangement. In a sublease-type arrangement, the initial Collocator(s) (Primary Collocator) shall charge any such Collocator (Resident Collocator) no more than the pro-rated share (based upon square footage used exclusively or in common) of AT&T's charges to the initial or primary Collocator(s). If two (2) or more Collocators who have interconnection agreements with AT&T utilize a shared collocation cage, AT&T will permit each Collocator to order UNEs to and provision service from that shared collocation space, regardless of which Collocator was the original Collocator.

Cageless Physical Collocation

AT&T will provide cageless physical collocation in any unused space in the eligible structure (i.e. space which is not occupied by AT&T personnel and/or occupied by or reserved for AT&T network equipment or needed for access to occupied or reserved space). AT&T will provide Collocators with a central entrance to the central office premises, and once inside, Collocators will have direct access to their equipment. AT&T will make cageless physical collocation space available in single-bay increments. AT&T will not require Collocators to use an intermediate interconnection arrangement, such as a POT frame. AT&T may, at its option, take reasonable steps to protect its own equipment, such as enclosing it with a wall or cage separating it from the cageless physical collocation space. AT&T may also require either an intermediate surge protection device or provide power from secondary distribution to limit risk to AT&T's primary power distribution network. If there is not sufficient space for AT&T to separate its equipment from the cageless physical collocation space by a wall or cage, AT&T may separate its equipment from the Collocator equipment by tape on the floor or other markings that are not physical separations. Accordingly, in the, Southwest, Midwest and West regions, AT&T will not provide a Collocator's personnel or agents with direct access to AT&T's main distribution frame, DSX environments or Fiber Distributing Frame.  In the Southeast Region Collocator's personnel or agents may have  direct access to AT&T's main distribution frame, DSX environments or Fiber Distributing Frame dependant upon a contractual basis with AT&T.

.

Adjacent Space Collocation

When space is legitimately exhausted inside an AT&T Eligible Structure, AT&T will permit Collocators to physically collocate in adjacent controlled environmental vaults or similar structures to the extent technically feasible. AT&T will permit Collocators to construct or otherwise procure such adjacent structure, subject only to reasonable safety and maintenance requirements, and zoning and other city, state and local regulations. The Collocator will be responsible for securing the required licenses and permits, the required site preparations, and retain responsibility for building and site maintenance associated with placing the adjacent structure. AT&T will permit the Collocator to place its own equipment subject to the same requirements and restriction as physical collocation in AT&T's eligible structure. AT&T reserves the right to assign the location of the designated space on AT&T premises where the adjacent structure will be placed.

At the Collocator’s request, AT&T will provide a standard offering of 100 AMPS of AC power to the adjacent structure from the Central Office power source when Central Office Switchboard AC capacity exists. AT&T will provide DC power in increments per applicable tariffs or ICA. At its option, the Collocator may choose to obtain an alternative source of AC power and/or DC power inside the adjacent structure. AT&T will provide power and physical collocation services and facilities to such adjacent structures, subject to the same non-discrimination requirements as other physical collocation arrangements in the Collocation Agreement.

Other Physical Collocation Arrangements

AT&T will provide other collocation arrangements that have been demonstrated to be technically feasible on other ILEC premises, unless the AT&T Eligible Structure cannot support the arrangement because of either technical reasons or lack of space. AT&T's denial to provide such a collocation arrangement, or offer an equally cost-effective arrangement, may only do so if it successfully rebuts the presumption of technical feasibility before the state commission that the particular premises in question cannot support the arrangement because of either technical reasons or lack of space.

Caged Physical Collocation in Central Offices

General

Because of AT&T's central office modernization program and AT&T's move toward shorter equipment framework (which will eliminate the need for ladders), Collocator facilities and equipment located in a central office must not exceed a height of seven feet (7').

AT&T will provide Caged and Shared Cage Floor Space in increments of 50 square feet. This minimum was established in order to allow for a door into the cage, one line-up of equipment bays and sufficient space between the cage enclosure and the bay(s) for technicians to install and maintain equipment. If the Collocator requests additional space to augment an existing cage, the collocator must order additional caged space in 50 square foot increments. If the Collocator requires an enclosure of less than 50 square feet to house only one or two bays,  refer to the section of this document titled “ Cageless Physical Collocation in Central Offices” below.

Dedicated Space designated for physical collocation will not be enclosed in a cage unless there is a specific request for that offering by the Collocator. If requested, the enclosure will conform to the standards for health, safety, Level 1 requirement as outlined in TP76200 and security to which  AT&T presently adheres within a central office environment.

Point of Termination (POT) Bay

An Interconnection Bay (i.e. Point of Termination (POT) Frame) is not required as the interconnection point. However, the Collocator may elect to install or request that the ILEC install an Interconnection Bay (Point of Termination (POT) Frame) either in its dedicated cage space or outside its cage in the AT&T-designated common area within the Eligible Structure Only if applicable in State Tariff or ICA & requested by the CLEC . If the Collocator requests an Interconnection Bay located outside its cage, the Collocator must request Cageless Collocation on the Physical Collocation Application and specify the square footage in addition to the Caged Collocation floor space requested. If the Collocator elects an ILEC provided POT frame, AT&T will install the POT frame and Interconnection Arrangement cables to the POT frame as designated by the Collocator on their application (Collocator's provided floor plan and front equipment view drawing). At job turn-over, the ILEC provided POT frame (including interconnection equipment) will be owned and maintained by the Collocator. If the Collocator elects to provide their own POT frame, the delivery of the interconnection cabling will be dependent on applicable tariff or ICA. When a Collocator request a POTLESS arrangement, interconnection cables will be installed by AT&T or the Collocator, dependent on applicable tariff or ICA. AT&T will provide cables with tagged cable ends to the Collocator's Dedicated Space (Caged location). All cable placements between the Collocator’s Dedicated Space and AT&T's equipment space will be performed by AT&T's Approved Tier 1 Supplier ,eligible for the scope of work.

Collocators can refer to Appendix section (Application section) of the CLEC Online web site https://clec.att.com/clec  for a copy of the Physical Collocation Application and Application Instructions.

Caged Collocation Cable Rack Standards

The build-out of Caged lower level frame racking and cable racks between the 7-foot high CLEC bays and the 7’6”-foot height is performed by the CLEC in the Caged Area, including bay lighting. (AT&T will provide middle and upper level frame and racking.) The CLEC will be required to provision all AC Power through their equipment and request their external communications access. The ILEC will provide all overhead superstructure and racking for physical and virtual collocation areas.

In the Caged area, the Collocator will be responsible for providing all lower level auxiliary framing and cable racks, including bay lighting in accordance to weight limitations of BSP 800-006-151/TP76409 and constructed to BSP 800-006-150/TP76408 requirements. The Collocator will provide cable rack systems which are no higher than 8 feet, measured from floor to underside of cable rack at the lowest point, and cable pileup no greater than 12 inches on cable rack, allowing sufficient clearance over the 7-foot high equipment bay layouts. Cabling within the Collocators Dedicated Space should be at the 8-foot level.

If the Collocator requests an interconnect bay located outside the cage, the cable racking from the Collocator’s interconnect bay to the Cage will stop at the cage egress point unless provisions are made to extend the rack at the Collocator’s cost. Power must be provided in a separate rack system from all other cabling. Timing leads may be provided in their own rack or permanently secured to the opposite sides of a cable rack. AT&T dedicated cable racks may traverse the Collocation space at the 9-foot level and higher and will not be used by a Collocator. The Collocator may elect to provide their own cable rack systems within their caged space or directly to the Collocator’s interconnect panel/block bay if located outside of the caged space only. AT&T will manage the cable rack requirements and placements throughout the Eligible Structure except for the Dedicated Space of the Collocator.

.

Shared Cage Physical Collocation in Central Offices

The Shared Cage will be considered to have all the same features and capabilities as the Standard Cage Area with the additional capability for two or more Collocators to make a joint application at the same time for a combined occupancy. For detailed information, refer to Caged Collocation Section.

Two or more Collocators selecting the Shared Cage option will pay their portion of the Dedicated Space (Cage) to AT&T.

Each Collocator selecting the Shared Cage option must provide a detailed floor plan layout to AT&T for reference as a common agreement point. AT&T will prorate the charge for site conditioning and preparation undertaken to construct the Shared Collocation Cage or condition the Dedicated Space, and allocate that charge to each Collocator based upon the percentage of total space utilized by each Collocator.

DC power will be engineered, furnished, and installed by AT&T for each Collocator of the Shared Cage. This is discussed in greater detail in the Power section.

If two (2) or more Collocators who have interconnection arrangements with AT&T utilized a Shared Collocation Cage, AT&T will permit each Collocator to order UNEs to provision service from that shared collocation space, regardless of which Collocator was the original Collocator.

The Collocator shall not assign or otherwise transfer, either in whole or in part, or permit the use of any part of the Dedicated Space by any other person or entity, without the prior written consent of AT&T, which consent shall not be unreasonably withheld. Any purported assignment or transfer made without such consent shall be voidable at the sole discretion of AT&T.

Collocators can refer to Appendix section of the CLEC Online web site https://clec.att.com/clec (Application section) for ordering Shared Cage Physical Collocation.

Cageless Physical Collocation in Central Offices

AT&T will provide cageless physical collocation in any Unused space in the eligible structure (i.e. space which is not occupied by AT&T personnel and/or occupied by or reserved for AT&T network equipment or needed for access to occupied or reserved space). AT&T will make cageless physical collocation space available in single bay increments.

Cable Racking- Cageless

Unlike Caged Physical Collocation, AT&T will provide the infrastructure auxiliary channel framing, cable racks, and lighting to support a bay layout architecture. AT&T will provide all levels/tiers of cable racks.

AT&T Southwest, West and Midwest  Regions only - Cageless Collocation will accommodate two generic sizes of floor space requirements or Dedicated Space. The standard bay footprint will accommodate a 7'0" bay framework (Zone 4 Unequal flange) equipped with a 5" front guard rail and a 2" rear guard rail, zone 4 anchors, and bay ground lead assembly. This standard bay will accommodate equipment no more than 15 inches deep. Due to egress needs, the minimum floor space requirements for this standard bay is 10 square feet. The large bay footprint will require a minimum of 18 square feet to allow for a 36-inch deep cabinet layout with swinging doors or equipment with greater than a 15-inch depth per AT&T Standards.

AT&T Southeast  Region only – With Cageless Collocation,  the CLEC will provide the exact square footage needed. The standard bay footprint will accommodate a 7'0" bay framework (Zone 4 Unequal flange) equipped with a 5" front guard rail and a 2" rear guard rail, zone 4 anchors, and bay ground lead assembly per AT&T Standards.

The Collocator will identify the type and quantity of equipment (by manufacturer) that it plans to install in its collocated space. This information will be furnished as part of the "Physical Collocation Application" under the equipment section: "Equipment to be Installed or Removed by Applicant". The "Physical Collocation Application" is included in Appendix section of the CLEC Online web site https://clec.att.com/clec.

The information provided by the Collocator will be used by AT&T engineering and architecture personnel to obtain the actual DC current drain, physical data (height, depth, weight, minimum front and rear aisle dimensions, heat release, etc.) and floor space determination. AT&T may require the Collocator to submit a "CLEC Equipment Review Request Form" when additional information is required for AT&T to complete the review of the Collocator's equipment. This form can be found in the Appendix section of the CLEC Online web site https://clec.att.com/clec.

The Collocator must provide a front equipment view drawing (bay elevation) which will aid in the understanding of the space requirements for the equipment to be placed. When the ILEC installs the interconnection cables, AT&T will install cables with tagged cable ends to the Collocator's Dedicated Space (Cageless location). All cabling run between the Collocator and AT&T will be performed by an AT&T Approved  Supplier, eligible for the scope of work.

.

##### Raceways & Turndown Provisioning

Inter-bay Fiber raceways  are the responsibility of the ILEC for all Central Office EF&I provisioning and management. The raceways  will be placed between 7'6" and 8'6" above CLEC assigned spaces. In the AT&T Southwest, West and Midwest  Regions only the CLEC at their discretion, may place their own Fiber raceways between adjacent bays in the same lineup only as long as the placement is within the equipment footprint of the assigned spaces and does not encroach on the 7'6" ceiling for CLEC equipment.  This does not apply to the Southeast region.  In  ALL regions, the CLEC cannot place fiber raceways or any equipment or racking above the 7'6" environment.

The responsibility for placement of turndowns is covered in the following chart ( Cable handoff  varies by region and ICA/Tariff)

| Ordering Situation | Technical Situation | Responsible Party to purchase and Install the Turndown |
| --- | --- | --- |
| CLEC orders Fiber to a specific bay | Raceway not in Place. ILEC provides Cable handoff | ILEC provides Raceway over all bays in the request and provides a Turndown to specific bay only |
| CLEC orders Fiber to a specific bay and then wants it placed to another bay in addition | Raceway not in Place, ILEC provides Cable Handoff | ILEC provides Raceway over all bays in the request and provides a Turndown to only that specific bay in the request, additional bays will be the responsibility of the CLEC |
| CLEC orders Fiber to a Specific Bay | Raceway not in Place, CLEC provides Cable Handoff | ILEC provides Raceway over all bays in the request. CLEC provides all Turndowns. |
| CLEC orders Fiber to a specific bay and then wants it placed to another bay in addition | Raceway not in Place, CLEC Provides Cable Handoff | ILEC provides Raceway over all bays in the request. CLEC provides all Turndowns. |
| CLEC orders Fiber to a specific bay | Raceway In Place ILEC provides Cable Handoff | ILEC provides Turndown to that specific bay only |
| Ordering Situation | Technical Situation | Responsible Party to purchase and Install the Turndown |
| CLEC orders Fiber to a specific bay and then wants it placed to another bay in addition | Raceway In Place, ILEC provides Cable Handoff | ILEC provides Turndown to only that specific bay in request, additional bays will be the responsibility of the CLEC |
| CLEC orders Fiber to a Specific Bay, CLEC Places cable | Raceway In Place, CLEC provides Cable Handoff | CLEC provides Turndown |
| CLEC orders Fiber to a specific bay and then wants it placed to another bay in addition | Raceway In Place, CLEC provides Cable Handoff | CLEC provides all Turndowns |
| CLEC wants to install direct cabling between two CLECs | Raceway in Place, CLEC provides the Cable Handoff | CLEC provides all Turndowns |
| CLEC wants to install direct cabling between two CLECs | Raceway in Place ILEC provides the Cable Handoff | ILEC provides all Turndowns |

Power

General

AT&T will follow its present power and grounding procedures and practices when providing collocation power. Collocators may not provide any power plant equipment of their own. Power plants are defined as DC power plants (operated by plant controllers and include primary power distribution) supported by rectifiers and storage batteries, AC backup plants supported by storage batteries, and standby AC plants (including engine-generators) within the eligible structure.

The AT&T provided power network is designed to ensure un-interrupted service in the event of a calculable loss of AC electric service provided by the electric utility. Unexpected power failures related to human error and equipment failure may occur but are rare.

Loads specified by the Collocator represent the peak current that will be imposed on a power feeder at any voltage within the emergency operating limits of the equipment and any normal operating condition (i.e. not a short circuit or other malfunction). Even though circuit design is based on peak current, DC power plant design sizing by all AT&T is based on demand management.

The design criteria of the DC power reserve is based on a normal operating voltage of approximately 50 to 56 VDC, with a minimum operating voltage (LV) of 42.64 VDC at the last point of ILEC responsibility. This may be either the CIPP panel or the raw ended cables turned over to the CLEC at completion of their order.

For central offices equipped with a stationary standby engine-alternator, a minimum of 4 hours of battery reserve shall be provided. The intent of this reserve is designed to protect telecommunication services operating on DC power during the transition from utility to generator-supplied AC power. Once in service, the stationary engine-alternator may be designed to carry the entire load (including essential, protected, building service and non-essential loads) within the eligible and on-site adjacent structure for a minimum of 72 hours. While normal cutover takes only minutes, the additional battery reserve is designed to take into account-failed starts, engine repairs and even portable generator transportation and hook-up time.

For central offices without a stationary standby engine-alternator, 8 hours (minimum) of battery reserve shall be provided. This reserve is designed to provide DC power until either the AC service is restored or a portable standby engine-alternator can be deployed at the location. Once in service, the connected portable genset should operate as a stationary standby unit (72 hours of continuous service).

For remote terminals, 8 hours of battery reserve is provided unless equipped with a stationary AC or DC generator. Locations equipped with a stationary generator will comply with the same guideline as a comparably equipped Central Office.

DC Power Arrangements (Caged, Shared Cage and Cageless)

Application requests of 100/200 AMP single feeds will require the use of 100/200 AMP Collocation Interconnection Power Panel (CIPP). The Collocator can request the ILEC to provide CIPP panel or provide its own, which must meet applicable safety requirements. The 50 Amp CIPP is optional at the request of the Collocator in AT&T Southwest, AT&T West and may be available in AT&T Midwest on an NSCR basis.   The 50 Amp CIPP is not  required under existing Southeast region agreements.

If required or desired, the CIPP will be provided by AT&T or the Collocator (Dependent upon applicable Tariff or ICA Authorization).

The Collocator must designate the CLEC's bay number location for each power arrangement cable, including CIPP if required or desired (Indicate the power cable handoff location(s) on the Front Equipment Drawing)

AC Power

AT&T will provide a breaker box for AC power for the geographic portion of the ILEC Building Structure.

Caged Arrangements: The ILEC provides AC outlets as part of the cage wall installation. Some states allow the CLEC to place their own cage walls (dependent on applicable tariff or ICA). The CLEC shall hire an AT&T Approved Supplier, eligible for the scope of work to place  cage walls. Cage lighting, cage ground, and AC outlets can also be placed by the CLEC as long as the CLEC uses an AT&T Approved Supplier, eligible for the scope of work.

Cageless Arrangement: The CLEC may place AC power for lights and duplex outlet kick panels in the bottom of the bays. The Supplier performing the work will be required to provide conduit into the cage structure area from the breaker box. When Cageless lineups are present, the first service provider in that lineup (ILEC or CLEC) will be required to bring conduit and AC cabling from the AC Junction Box to that bay. Subsequent bays provided by either the CLEC or ILEC will connect to the previous AC outlet arrangements on the preceding bay. It is the AT&T Approved Supplier’s, eligible for the scope of work responsibility to place the proper material to safely by-pass assigned, future bay spaces within a lineup as directed on the floor plan in order to place AC to their assigned bays.

Standard AC circuits consists of a 20-amp service. Emergency lighting will also be provided by AT&T. AT&T will provide a breaker box for AC power. If the Collocator requests AT&T to provide AC power cable for lights and duplex outlets in kick panels in the bottom of the bays other than the normal standard policy,  time and material charges will apply. The Supplier performing the work will be required to provide conduit into the Collocator’s Dedicated Space (cage or cageless equipment bay) area from the breaker box.

Essential AC Power

Essential AC power is generally inverted DC power, protected by the DC plant batteries as other telecommunications systems are. It will be provided by AT&T only under prices, terms, and conditions as determined by Custom Work Order or as provided by tariff or ICA  (where applicable).

.

TP76200 DC Powering of Equipment

DC power is generally provided to the Collocator as “power in common” and is shared with AT&T and other Collocators. A Collocator’s equipment shall be capable of operating in the power systems environment described in the current issue of the TP76200.

DC Distribution Power Arrangement

Dependent on applicable tariff or ICA, AT&T may provide standard power arrangements specified in the Collocator’s application. The requested feeds should be sized to handle the peak current the equipment will draw at any voltage within the emergency operating range and any normal operating condition (i.e. not a short circuit or other malfunction). Even though circuit design is based on peak current, DC power plant capacity management at AT&T is based on demand.

DC Power Delivery Arrangement

DC power arrangements will be provided as bare ended cables in the location of choice as indicated by the Collocator in their application per ICA/Tariff and Region.

10 - 50 Amp DC Power Arrangements:  AT&T Southwest, West,  Midwest Only

The Collocator is no longer required to provide a 50 AMP CIPP (DC power panel) when terminating DC Power Arrangements of 50 amps or less within their dedicated space.

- The Collocator may choose to provide their own DC power distribution panel that meets NEBS Level 1-safety requirements. AT&T will provide bare ended tagged cables in this application. The Collocator will be responsible for terminating the cables on the DC power panel.

Or (Optional,) (Refer to table below)

- The Collocator may choose to allow AT&T to provide a termination (CIPP) panel, fully terminated on the input side, in a Collocator designated location.

- AT&T standard 50 AMP CIPP is the  PECO II Collocation Interconnect Power Panel(s) (CIPP),   Refer to external drawing ATT-P-05911-E or the panel can be order from Trimm Inc. 407 Railroad St Butner, NC 27509. 1-800-298-7466 Ricky Brummitt or Will Newton ordering information is TRIMM Collocation Interface Power panel (CIPP panel) - part #937200111 - OIN # ATT.PWPYADARRA - PAN 2013-003..

- The Collocator must notify AT&T at least five (5) business days in advance of the date they want AT&T to perform the installation of the CIPP in the Collocator’s designated bay.

100/200 Amp Arrangements:  ALL Regions

100/200 amp power arrangement cabling must be terminated in a termination panel (CIPP) which may be provided as follows:

- The Collocator may choose to provide their own termination (CIPP) panel that meets the AT&T approved product’s operating and circuit protection capabilities, as well as TP76200 Level 1 safety requirements. It must also be reviewed by the AT&T technical staff to confirm it provides the same level of network safety and security as the AT&T provided CIPP. The Collocator will be responsible for terminating the cables on the CIPP.

Or  (Optional,) (Refer to table below)

- The Collocator may choose to allow AT&T to provide a termination (CIPP) panel, fully terminated on the input side, in a Collocator designated location per ICA/Tariff and Region.

- AT&T standard 100/200 CIPP is the PECO II 200 AMP  PECO II Collocation Interconnect Power Panel(s) (CIPP),   Refer to external drawing ATT-P-05911-E  or the panel can be order from Trimm Inc. 407 Railroad St Butner, NC 27509. 1-800-298-7466 Ricky Brummitt or Will Newton ordering information is TRIMM Collocation Interface Power panel (CIPP panel) - part #937200111 - OIN # ATT.PWPYADARRA - PAN 2013-003..

- The Collocator must notify AT&T at least five (5) business days in advance of the date they want AT&T to perform the installation of the CIPP in the Collocator’s designated bay.

All power termination locations, whether or not a CIPP is required, shall be clearly identified on the front equipment drawing the Collocator provides with the application.

CIPP panels shall be clearly identified on the drawings to allow AT&T engineers to either install or cable to the proper frame location.

The Table below provide information per regions/ICA's. All information in the table is dependant on State Tariff or ICA.

| Region/Contract | Function | Application | Action |
| --- | --- | --- | --- |
| AT&T- Southwest, Midwest and West Region with 12 state generic ICA |  |  |  |
|  | AT&T Providing CIPP Panels | New CLEC Application | AT&T Provides upon request by the CLEC |
|  | AT&T Providing CIPP Panels | Augment CLEC Application | AT&T Provides upon request by the CLEC |
|  | AT&T Installation of CIPP Panels | New CLEC Application | AT&T Provides upon request by the CLEC |
| Region/Contract | Function | Application | Action |
|  | AT&T Installation of CIPP Panels | Augment CLEC Application | AT&T does not provide – Not Applicable |
|  | AT&T Termination of Power Cables on AT&T provided CIPP Panels | New CLEC Application | AT&T Provides termination on the AT&T provided CIPP Panel |
|  | AT&T Termination of Power Cables on AT&T provided CIPP Panels | Augment CLEC Application | AT&T does not provide or terminate power cables |
| Region/Contract | Function | Application | Action |
|  | AT&T Termination of Power Cables on CLEC provided CIPP Panels | New CLEC Application | AT&T does not terminate to CLEC provided CIPP panel. Tag and handoff to bay requested only |
|  | AT&T Termination of Power Cables on CLEC provided CIPP Panels | Augment CLEC Application | AT&T does not terminate to CLEC provided CIPP panel. Tag and handoff to bay requested only |
| AT&T Southeast Region |  |  |  |
|  | *** currently SE does not require CIPP panels per existing ICA and Tariffs |  |  |
| ALL Regions with 21 State Generic ICA |  |  |  |
|  | CLEC providing & installing CIPP panels CLEC termination of power cables on CIPP Panel | New or Augment Collocation Application | AT&T provides CLEC ordering information to order CIPP panel directly from PECO II (refer to drawing ATT-P-05911-E for detail information. The panel can also be order from Trimm Inc. 407 Railroad St Butner, NC 27509. 1-800-298-7466 Ricky Brummitt or Will Newton ordering information is TRIMM Collocation Interface Power panel (CIPP panel) - part #937200111 - OIN # ATT.PWPYADARRA - PAN 2013-003. IMPORTANT: CLEC must contract with an AT&T 21 STATE AIS Tier 1 to run the power distribution feeder cable |

#### DC Power Provisioning

It is assumed that the loads specified by the Collocator take into account the peak current that will be imposed on a power feeder at any voltage within the emergency operating limits of the equipment and any normal operating condition (i.e. not a short circuit or other malfunction). Even though circuit design is based on peak current, DC power plant capacity management by AT&T is based on demand management.

The demarcation (or first termination) for power will either be the CIPP panel or the raw cable ends, depending on the engineering requirements and regions. The Collocator is also responsible for terminating and distributing power to equipment located in their equipment bays within the established guidelines.

In caged, shared and cageless applications, the Collocator is responsible for notifying Collocation Services when the power is terminated and that it is ready to be “powered up”.

Where the 50 AMP CIPP is supplied by AT&T, the panel will be equipped with two TPS-type fuse blocks (3-amp to 70-amp capacity each), shunts, volt and amp meter and alarm relay. The AT&T engineer shall provision three (3) fuses (one for each fuse block and one spare) sized to match the requested power feed. The Collocator will determine the panel location. The panel will be equipped with space for eight (8) two-hole  connections. [Note: Power and battery return connections must be made with a two-hole compression connector.] Panel shall be  PECO II Collocation Interconnect Power Panel(s) (CIPP), TRIMM Collocation Interface Power panel (CIPP panel) - part #937200111 - OIN # ATT.PWPYADARRA - PAN 2013-003.or approved equal.   Refer to external drawing ATT-P-05911-E.

Where the 100/200 AMP CIPP panel is supplied by AT&T, the panel will be equipped with two TPL-type fuse blocks (70 amp to 250 amp capacity), shunts, volt and amp meter and alarm relay. The AT&T engineer shall provision three (3) fuses (one for each fuse block and one spare) sized to match the requested power feed. The two sets of output termination landings located in the rear of the panel are drilled for two hole connectors based on one inch centers. [Note: Power and battery return connections must be made with a two-hole compression connector.] The Collocator will determine the panel location. Due to the panel size and cable entry requirements, the panel is not designed for cabinet mounted applications. Panel shall be PECO II Collocation Interconnect Power Panel(s) (CIPP), TRIMM Collocation Interface Power panel (CIPP panel) - part #937200111 - OIN # ATT.PWPYADARRA - PAN 2013-003.or approved equal.   Refer to external drawing ATT-P-05911-E.

.

DC Power provisions are based on the following assumptions, using existing design criteria used in building the DC power plant:

- Designed voltage drop shall be measured from the DC power plant batteries to the CIPP -48 Volt power fuse panel or the end of the bare cable lengths. Designed voltage drop shall not exceed 1.0 Volts for the supply run and 1.0 Volts for the return run (total loop/circuit voltage drop of 2.0 Volts maximum).

- For battery discharge conditions, minimum volts per cell (mvpc) shall be set at 1.86 Volts (44.64 final string voltage or 42.64 Volts at the last point of AT&T responsibility).

To furnish power to the Collocator, AT&T will install power cables from a power plant distribution bay to a CIPP (for 100/200 amp feeds) or from a convenient BDFB (based on location, capacity and service) to bare-ended cables (refer to your contract for increments). In situations requiring the CIPP, the Collocator will obtain its DC power by cabling to the rear (distribution) side of the power panel. Where bare-ended cables are supplied by AT&T, the Collocator has the responsibility to make the proper termination, based on cable size and terminating equipment configuration.

To meet these needs, DC power to the Collocator will be as follows:

- All DC power arrangements to Collocators will be provided as dual (A & B) feeds, each capable of carrying the total current load if one side fails for any reason. For 10/20/30/40/50 amp circuits, the Collocator may elect to have AT&T to originate power feeds at a BDFB and terminate as bare-ended cables at a convenient point on the cable rack over or near the Collocator’s assigned cage or footprint. When the power feeds originate at a primary distribution point (power plant distribution bay), unless the power plant is dedicated to Collocation service, the feeds will terminate at an intermediate (secondary) distribution point, the 50 AMP CIPP. For small loads, the 50 AMP CIPP is optional. The Collocator will designate the location where the 50 AMP CIPP will be installed in their cage or footprint. For the large size feeds, because the 100/200 AMP CIPP is required in all instances, the Collocator has the option of installing the 100/200 AMP CIPP, or letting AT&T install the panel. Once in place, the Collocator can terminate on the back of the CIPP and run their power feeds to their own frames. Final coordination is required to install the upstream fuses, confirm proper connections and polarity, and finally install the downstream fuses.

- Unless otherwise requested by a Collocator, all Collocation power is part of the Common Bonding Network (CBN). For the AT&T engineer, fuse sizing is based on the Collocation request. It is the Collocator’s responsibility to determine maximum equipment load and request the proper sized circuit(s). A 25-amp fuse protects a 20-amp circuit, a 40-amp fuse protects a 30-amp circuit, and a 60-amp fuse protects a 50-amp circuit.

- In situations where a CIPP panel is not requested or required, bare ended cables will be supplied at the bay of choice determined by the Collocator. In these situations Refer to external AT&T drawing ATT-P-05911-E for detailed information.

- Where the optional 50 AMP CIPP is supplied by AT&T, the panel will be equipped with two TPS-type fuse blocks (3 amp to 70 amp capacity each), shunts, volt and amp meters, and alarm relay. The AT&T engineer shall provision three (3) fuses (one for each fuse block and one spare) sized to match the requested power feed. The Collocator will determine the panel location. The panel will be equipped with space for eight (8) two-hole connections. [Note: Power and battery return connections must be made with a two-hole compression connector.]  Panel shall be PECO II Collocation Interconnect Power Panel(s) (CIPP), TRIMM Collocation Interface Power panel (CIPP panel) - part #937200111 - OIN # ATT.PWPYADARRA - PAN 2013-003 or approved equal.  Refer to external drawing ATT-P-05911-E.  In situations using a CIPP panel Refer to external AT&T drawing ATT-P-05911-E for detailed information.

- Where the 100/200 AMP CIPP is supplied by AT&T, the panel will be equipped with two TPL-type fuse blocks (70 amp to 250-amp capacity), shunts, volt and amp meters, and alarm relay. The AT&T engineer shall provision three (3) fuses (one for each fuse block and one spare) sized to match the requested power feed. The two sets of output termination landings located in the rear of the panel are drilled for two hole connectors based on one inch centers. [Note: Power and battery return connections must be made with a two-hole compression connector.] The Collocator will determine the panel location. Due to the panel size and cable entry requirements, the panel is not designed for cabinet mounted applications. Panel shall be PECO II Collocation Interconnect Power Panel(s) (CIPP), TRIMM Collocation Interface Power panel (CIPP panel) - part #937200111 - OIN # ATT.PWPYADARRA - PAN 2013-003 or approved equal. Refer to external drawing ATT-P-05911-E.   In applications using a CIPP panel,  Refer to external AT&T drawing ATT-P-05911-E for detailed information.. Cabinet mounting of this panel is not recommended due to the size of the panel and power cables and the limited space in a cabinet allowed for cable entry.

- This CIPP is equipped with an alarm circuit. When a CIPP is provided and located in the Collocator equipment area, surveillance of alarms associated with this panel is the responsibility of the Collocator.

Protector Sizing Guidelines (ALL Regions)

Whether in a Caged or Cageless application, the following criteria shall be followed to insure maximum reliability: Refer to external AT&T drawing ATT-P-05911-E for detailed information.

Additional Power Arrangements

Additional Power Arrangements must be requested by submitting an Application for Physical Collocation (Refer to  Appendix A in the Appendix section of this handbook). The quantity and type of power arrangements being requested must be specified in Power section of the application by the Collocator and provided to AT&T. This will allow AT&T to engineer, order and install additional cabling, power plant equipment and etc., and thus avoid potential service conditions (region specific).

Distribution of Power in Collocation Area

The Collocator shall either request individual power feeds for each piece of equipment or provide an abbreviated form of power distribution. BDFBs, even mini-BDFBs, duplicate equipment already installed in AT&T's network in size, scope and functionality. Smaller power distribution units (PDUs) can provide adequate power distribution in a compact and convenient size.

.

Non Standard Requested RSM Arrangements

The Collocator may request remote switch module (RSM) power arrangements. Unless otherwise indicated on the application, these loads will be in the Isolated Bonding Network (IBN). The same power increments are available (refer to your contract for increments), but in this situation all feeds will originate at the power plant and terminate at a CIPP in the Collocator’s cage or footprint. The power plant is the only source where you can get an isolated ground and the CIPP is the only means of protecting the power plant.

Non-standard Power Arrangements

Any power request outside of the Tariffed feeds and the integrated bonding network is considered a “non-standard” power arrangement. All non-standard power arrangements are provided on an individual case basis (ICB), (ICB’s are only available in the AT&T Southwest, West and Midwest regions. In the Southeast region this would require an amendment to the contract.) with timelines and costs re-negotiated for each case.

Grounding

General

AT&T will furnish and install a minimum #2 AWG conductor extended from a point on the central office ground system into the cage or to the Collocator’s cageless dedicated space. This may be a CO GRD or OPGP bus bar or a point on the horizontal equalizer system of equal or greater size. In Caged Collocation, this conductor will be routed and secured to two sides of the cage near the top of the cage sections.

Furnished Ground

AT&T will furnish and install:

- A #6 AWG branch conductor from the #2 AWG to the optional Collocators interconnect panel/block frame, and

- In Caged Collocation, a #6 AWG branch conductor from the #2 AWG to the optional cage’s metal framework.

Parallel Type Connectors

Using crimp type parallel connectors, the Collocator shall extend grounding conductors from the #2 AWG to their equipment as needed. These shall be a minimum #6 AWG insulated copper conductors.

Cage Bonding

If the cage sections are not mechanically joined (bolted and/or clamped together), each section shall be bonded to an adjoining section with a minimum #6 AWG conductor. This should only occur when a building structural component, such as a column, is interposed between cage sections.

IBN Environment

If the Collocator intends to use equipment requiring an IBN environment, the site must first be evaluated to determine if the collocation area conforms to the applicable requirements for an IBN environment. Any prospective cage used for IBN equipment must meet all of the following rules:

- Equipment connected to an MGB must be located within one vertical floor of the floor containing the MGB. Example: An MGB exists on the 3rd floor of a building. Equipment served by this MGB may only be located on the 2nd, 3rd or 4th floor.

- Equipment must be located within 200 conductor feet of a central office ground (CO GRD) bar or an office principal ground point (OPGP) bus bar. Example: An MGB is 95 conductor feet from a CO GRD bar. All IBN equipment served by this MGB must be within 105 conductor feet of the MGB.

- A power plant may be served by only a single MGB.

Grounding IBN Equipment

All IBN equipment must be grounded per equipment manufacturer requirements and those in BSP 812-000-027/TP76416. Among other things, this means that no IBN equipment may be bonded to the main cage conductor. Note: A collocation cage may contain both CBN and IBN type equipment, but no direct electrical connection may exist within the cage between the two types of equipment grounding systems. Any interconnection between grounding systems may only be made via the MGB.

Cageless Collocation

All applicable grounding requirements in BSP 812-000-027/TP76416 shall be applied to all cageless collocation equipment. Equipment grounding may be arranged for the Isolated Bonding Network (IBN), the Common Bonding Network (CBN), or both.

Non-standard Power Arrangements

A Non-standard Power arrangement must be specified if the Collocator’s request includes other than common bonding network (i.e. isolated ground).

Note: All applicable grounding requirements in BSP 812-000-027/TP76416 shall be applied to the equipment within the collocation cage or cageless dedicated space. Equipment grounding may be arranged for the Isolated Bonding Network (IBN), the Common Bonding Network (CBN), or both.

Synchronization (Caged, Shared Cage and Cageless) (All Regions)

This section describes the policy of AT&T regarding the assignment and installation of timing leads sourced from AT&T Timing Signal Generators (TSG) to a collocator’s network element. Generic Methods and Procedures for the assignment and installation of timing leads to a collocator are included in this document.

Effective May 1, 2008, the previous policy requiring a T-Carrier Bridging Office Repeater (TBOR) on a DS1 timing signal lead to a collocator’s network element is rescinded. Going forward, the standard installation of a timing lead to a collocator’s equipment will not include a TBOR.

General:

Interoperability of digital networks requires that there be a standard reference frequency to align the various network elements. In North American networks, this frequency standard is traceable to Universal Coordinated Time (UTC) at an accuracy of at least plus/minus 1 part in 100 billion (+/- 1e X 10-11). In the North American timing hierarchy, this level of accuracy is known as Stratum 1. Any two networks can interoperate successfully if each network has a frequency reference that meets this standard. Under a worst case situation, where one network is at the positive limit, and the other is at the negative limit (i.e. 2e X 10-11 frequency offset), networks interoperating at DS1 rates will experience 1 frame slip in about 72 days. In actual practice, Stratum 1 Primary Reference Source (PRS) systems employed in telecom carrier networks are much more accurate than Stratum 1 minimum.

It is the responsibility of a collocator to understand synchronization standards, the synchronization needs of their own network, and to provide a suitable timing reference to all collocator owned digital network elements that will interconnect to other networks at synchronous interfaces such as DS1, SONET optical rates, etc.

There are several ways a collocator can accomplish a Stratum 1 traceable timing reference;

• Install a Primary Reference Source (PRS) that does not require an externally mounted antenna (e.g. a Cesium PRS).

• ‘Line time’ a TDM or SONET network element from an incoming signal that is traceable to a PRS.

• Extract a Derived DS1 timing signal from the optical line rate of an incoming optical signal that is traceable to a PRS.

Dependent on tariff or Interconnection Collocation Agreement (ICA), the collocator may elect to request timing leads sourced from the AT&T TSG.

At a collocator’s request, and where an applicable tariff or ICA is in place, AT&T will supply a DS1 timing reference or multiple DS1 timing references to the collocator, subject to the pricing of applicable tariffs or ICA and the policies and procedures herein.

The AT&T Southeast region process for allowing a collocator to place a Primary Reference Source system that utilizes an external antenna (e.g.; a LORAN or GPS based PRS system) has been discontinued. Existing GPS systems placed by collocators are grandfathered and may remain in service. Going forward, collocators operating in the AT&T Southeast region will have the option to apply for DS1 timing reference leads in the same manner as the AT&T Southwest, Midwest and West regions.  .

The remainder of this section addresses policies, and methods and procedures for providing AT&T TSG sourced DS1 timing references to a collocator.

A. Collocator Responsibilities:

The AT&T synchronization network is a complex, costly, and extremely critical component of the network infrastructure. The collocator is advised to apply professional standards of conduct, and due diligence, when connecting, disconnecting, or testing on AT&T supplied timing reference circuits. Repeated alarms on the AT&T TSG due to collocator activity could result in charges to the collocator and possible loss of this service.

The standard timing signal supplied from the AT&T TSG shall be a D4 (Superframe) DS1, all 1s, meeting GR-378 and GR-499 specifications.

The collocator shall specify on the application for timing leads –

- The ‘drop-off’ location desired for the timing lead(s) to be provided to, and a reasonable length of timing cable needed for the collocator to extend the lead(s) into the collocator’s equipment location. In no case will the timing cable length exceed 655 feet.

2. The number of timing leads required.

3. The collocator Access Customer Name Abbreviation (ACNA), and relay rack or bay number for each timing lead or set of leads when requested as a pair. This information is needed to document the port assignments, and to aid in isolation of any port alarms.

The collocator is responsible for selecting, and optioning, the collocator equipment to accept a GR-499 compliant DS1 timing signal. Refer to GR-499 for applicable testing standards. AT&T is not responsible for the performance of a timing signal into a non-compliant interface. Requests for assistance from AT&T to resolve a timing issue with AT&T supplied DS1 timing references that result in a finding of trouble on the collocator interface will obligate the collocator to pay AT&T time and material charges where applicable.

The collocator’s AT&T Approved Tier 1 supplier shall provide a properly executed Method of Procedure notification to the AT&T Local Field Operations – In (LFO-IN) forces stating the date and time that the collocator plans to terminate the timing leads onto the collocator’s equipment. The collocator’s Tier 1 installation supplier will extend the timing cables to the network element. At the time designated, the collocator’s Tier 1 supplier will cut the timing cable to length, and immediately terminate the cable to the network element that has been pre-conditioned to supply a GR-499 compliant signal termination.

The collocator shall notify AT&T in advance of any planned disconnection of timing leads. This is important for three reasons; it stops the billing, it prevents possible TSG port alarms due to an open circuit condition, and notifies AT&T to recover the TSG port for reassignment.

B. AT&T Responsibilities:

The quality of timing signal, timing cable, etc. shall be the same as for AT&T network elements. The collocator will not get a timing reference that is inferior in any respect to that provided for AT&T network equipment. However, AT&T does not guarantee that a timing circuit supplied from an AT&T TSG will be Stratum 1 traceable 100 percent of the time.

AT&T GNFO-CO will generally not need to be engaged in the installation of timing leads to a collocator. In the event of a port alarm, the GNFO-CO technician shall follow existing M&Ps to isolate the source of the alarm. If the trouble is caused by collocator activity, including disconnect, the technician shall report the incident to the GNFO-CO supervisor, who will in turn notify the AT&T Collocation Manager for that site. The AT&T Collocation Manager shall determine if the collocator will be billed for the trouble resolution.

C. AT&T Approved Installation Supplier, eligible for the scope of work, – Detail Engineering Responsibilities:

Assign DS1 D4/Superframe ports for all standard collocator requests. Assign Extended Super Frame ports only as directed by the Area Synchronization Coordinator.

Dedicated timing output cards are not required. Timing leads for collocator equipment may be assigned to any available port on a TSG output card.

Specify AT&T standard red jacketed 1175A cable for all timing leads.

D. AT&T Approved Installation Supplier, eligible for the scope of work, – Installation Responsibilities

Place the timing cable(s) to the designated ‘drop-off’ point, following standard procedures for diverse routing, securing the cable(s), etc. Be sure to allow sufficient cable per the collocator’s request so that the cable can be extended to the collocator NE.

Tag the network element end of each cable with the ACNA, NE relay rack/bay number, TSG relay tack number, TSG shelf/card/port.

Butt strip about 3 inches of jacket and shield from the NE end of each timing cable. Strip about 1 inch of insulation from tip and ring conductors. Using 3 full twists per side, connect a 100 Ohm (+/- 5% tolerance), 1/4 Watt resistor between the tip and ring conductors. Carefully fold the resistor and tip/ring conductors such that the resistor is in line with the cable, and cover the cable end and resistor with heat shrink tubing. The purpose of this resistor is to provide a temporary signal termination for the TSG pending the final termination by the collocator.

At the TSG, prepare the timing cables for termination per AT&T standard practice. Before terminating each cable, verify the tip to ring loop resistance of each cable is between 95 and 130 Ohms, using a digital Volt Ohmmeter. This test validates the correct installation of the termination resistor at the network element end of each cable. Once the loop resistance test validates the far end termination, terminate the timing cable onto the TSG wire wrap panel.

Dependent on Tariff or ICA, the Demarcation point will be at the AT&T designated tie-down point at the TSG wire wrap panel.

Interconnection Requirements and Arrangements (Caged, Shared Cage and Cageless)

The Collocator can refer to the Physical Collocation Application, Interconnection Requirements Section found in Appendix A of the CLEC Online web site, https://clec.att.com/clec/  for all individual Collocator Interconnection Requirements, and populate the quantity of interconnect bays, panels, circuits, and timing requirements needed.

Table - Ordering Increments by State Tariff (example)

| Type |  |
| --- | --- |
|  | AR, KS, MO, OK, TX, NV, MI | IL, IN, OH, WI | CA | Alabama, Florida, Georgia, Kentucky, Louisiana, Mississippi, North Carolina, South Carolina, Tennessee |
| DS0 (Copper Cable Shielded Pairs) | 100 | 100 | 1 | Actual Qty Ordered |
| DS0 (Copper Cable Non-Shielded Pairs) | 100 | 100 | 1 | Actual Qty Ordered |
| DS-1 Shielded Cable (circuits) | 28 | 56 | 1 | Actual Qty Ordered |
| DS-3 (circuits) | 1 | 1 | 1 | Actual Qty Ordered |
| Fiber optics (strands) | 24 | 24 | 12 | Actual Qty Ordered |

- Qty Ordered should be total of Ordering Increments (e.g. 500 for 500 VG pairs, 56 for 56 DS-1 shielded)

- Shielded cable = shielded exterior sheath required

Point of Termination (POT) Interconnection Panel Information:

If the Collocator elects to install interconnection panels and POT bay(s), they may be provided and installed on the initial arrangement application by either the Collocator or AT&T   (Dependent upon applicable Tariff or ICA authorization). The Collocator must indicate the number and type of interconnection panels, the specific CLEC bay location panels are to be installed (the Front Equipment View (FEV) drawing is required). AT&T will utilized this FEV drawing when placing extending ILEC provided interconnection cabling to the Collocator's Dedicated Space.

Notice

The Collocator must specify the location of the interconnect panels within the Collocator's bay on the front equipment drawings submitted with their application.

AT&T Standard Point of Termination (POT) Equipment

A. AT&T POT Equipment Standards

Point of Termination equipment is handled as a Grandfathered Option for the ILEC to provide at the request of the CLEC. This section is provided to specify the AT&T standard equipment to be used and not to be substituted in AT&T C.O.’s. These products were being used at the issuance of the Cageless Collocation Mandate (FCC 99-48).

1. Voice Grade Facilities and xDSL:

Manufactured by ADC

.

QCP-W10X20-5 Size: 6” x 23” x 4” panel Provides for 500 cable pairs

Standard Equipment.

QCP-W-C Size: 6” x 23” x 4” panel Provides for placement of empty chassis

QCP-W10X20-1

Provides one snap in 100 pair module to be placed in QCP-W-C. 5 modules will fit the QCP-W-C.

2. DS1 Interconnect

Manufactured by ADC

.

DD1-351151 DDP-1 for 84 DS1 Size: 4” x 23” x 5” panel

DD1-100005 Jack Access Card (5 cards per DDP-1 panel)

3. DS3/STS1 Interconnect

Manufactured by ADC

D3C-234001 DS3/STS1 24 port panel using BNC connectors. Size: 4” x 23” x 3”

D3M-BM2001 DS3/STS1 Module, BNC Access for IN, OUT, CLEC in, CLEC OUT with dual monitor Size: 4” x ½” x 3”

Fiber Optic Splitter Terminations

| DESCRIPTION MANUFACTURER ID | MODEL PART |
| --- | --- |
| LDC-21B-B-58-SB LDC (Vertical) Coupler Module/Dual - SC | Module, 1x2 90/10 2 Splitters SC-UPC |
| ATN-58-TM Fiberoptic SC Ultra PC Terminator | Terminator, Fiberoptic SC-UPC |
| LDC-CMH-072 LDC (Vertical) Optical Splitter Housing; Rack Mount | FDF Splitter Housing, 12 Slots |

| Fiber Optic Splitter Terminations Manufactured by Corning Cable Systems (previously Siecor), the distributor is listed below the product: |
| --- |
| MODEL PART | ACCOUNT COST | AT&T CLEI/PID | DESCRIPTION MANUFACTURER ID |
| Module, 1x2 90/10 2 Splitters SC-UPC | 357C | 300025467 | LDC-21B-B-58-SB LDC (Vertical) Coupler Module/Dual - SC |
| Terminator, Fiber Optic SC-UPC | 357M | 300029758 | ATN-58-TM Fiberoptic SC Ultra PC Terminator |
| FDF Splitter Housing, 12 Slots | 357C | LGCXYPA2RA 300029766 | LDC-CMH-072 LDC (Vertical) Optical Splitter Housing; Rack Mount |

B. Installation and Augment Policy on Standard Bay/Cabinet (POT) with Interconnect POT Panels

(ALL Regions)

When interconnection fiber terminations are requested on an Initial CLEC collocation application, and AT&T is terminating the fiber to a Fiber/Splitter panel, the following applies: The splitter plug-in is driven by the service order process. Therefore, AT&T will coil and tag the fiber cable that was placed (based on the number of optical cross connects requested on the collocation application), and only terminate on the fiber/splitter panel when the CLEC orders circuits associated with the identified fiber cable.

Function Application Type Action AT&T Providing Interconnect Panels Initial CLEC Application AT&T Provides - Only if applicable in State Tariff or ICA & requested by the CLEC AT&T Providing Interconnect Panels Augment CLEC Application AT&T does not provide - Not Applicable AT&T Installation of Interconnection Panels Initial CLEC Application AT&T Provides - Only if applicable in State Tariff or ICA & requested by the CLEC AT&T Installation of Interconnection Panels Augment CLEC Application AT&T does not provide - Not Applicable AT&T Termination of Interconnection Cables on AT&T provided POT Panels Initial CLEC Application AT&T Provides termination to AT&T provided panel - Only applicable in State Tariff or ICA & requested by the CLEC AT&T Termination of Interconnection Cables on AT&T provided POT Panels Augment CLEC Application AT&T does not provide - Not Applicable AT&T Termination of Interconnection Cables on CLEC provided POT Panels Initial CLEC Application AT&T does not terminate to CLEC provided panel. Tag and hand-off to bay requested only (AT&T Southwest, West and Midwest region only) AT&T Termination of Interconnection Cables on CLEC provided POT Panels Augment CLEC Application AT&T does not terminate to CLEC provided panel. Tag and hand-off to bay requested only(AT&T Southwest, West and Midwest region only)

Table - Capacity of AT&T Standard Interconnect Panels

| Std Interconnection Panels | Capacity Per Panel |
| --- | --- |
|  | AR, KS, MO, MI, NV, CA IL, IN, OH, WI,TX,OK Alabama, Florida, Georgia, Kentucky, Louisiana, Mississippi, North Carolina, South Carolina, Tennessee |
| Copper Cable | 500 |
| (Height in Inches) | 6 |
| DS-1 | 84 |
| (Height in Inches) | 4 |
| DS-3 | 24 |
| (Height in Inches) | 4 |
| Fiber optics (strands) | 24 (SC-SM) |
| (Height in Inches) | 7 |

In the AT&T Southwest, West and Midwest regions the Collocator may elect to have AT&T extend the quantity of DS0, DS1, DS3, and/or fiber Interconnection Arrangements to the Collocator's Dedicated Space (or optional Collocator’s interconnect panel/block) as specified by the Collocator's Physical Collocation Application (. Depending on the Collocator’s design and AT&T requirements, AT&T will provide dedicated cabling from the Collocator's Dedicated Space to AT&T's DS0 frame or fiber distribution frame. AT&T will provide cables with tagged-cabled ends to the Collocator’s Dedicated Space for the Collocator to terminate on their equipment. AT&T will provide the Collocator a unique Additional Point of Termination (APOT) or Carrier Facility Assignment (CFA) information for ordering UNEs via the ASR process.

In the AT&T Southeast region the CLEC must hire an Approved Installation Supplier, eligible for the scope of work, to perform all CLEC installation work functions.  AT&T will provide the Collocator a unique Additional Point of Termination (APOT) or Carrier Facility Assignment (CFA) information for ordering UNEs via the ASR process.

Interconnection Arrangement Demarcation Point & Test Access

In the new Caged and Cageless Collocation Areas, the cable demarcation point for the AT&T ILEC provided interconnection cabling has changed from the Point of Termination (POT) Panel drop jack going toward the CLEC to the end of the cable handed off to the Collocator's designated bay within the collocator's footprint. AT&T shall designate the point(s) of termination within the Eligible Structure in which the Dedicated Space is located as the point(s) of physical demarcation between the Collocator’s network and AT&T's network. In addition, both AT&T and the Collocator will be responsible for cable maintenance and other ownership obligations and responsibilities on its side of that demarcation point. The demarcation point for all services will be the Collocator's last test access point of the cable end that terminates on the Collocator’s equipment. The standard last test access point for AT&T personnel will be the interconnection point at the AT&T equipment or DSX/frame network. This is where the cable coming from the Collocator’s equipment is terminated on the ILEC end. AT&T will terminate and test all interconnections if the interconnection panels are provided by AT&T. AT&T will not terminate or test interconnections if the Collocator provides the interconnection cable or interconnection panels. Refer to Installation Section in this handbook for Test and Acceptance Procedures.

ILEC Provided Interconnection Cable hand-offs:

The actual handoff of services terminates at the end of the connector or equivalent following the table below:

| Service Type | Cable Type | Termination/Demarcation |
| --- | --- | --- |
| DSO/VF | Copper 50/100 pairs | Tagged Only |
| DSL | Copper 50/100 pairs | Tagged Only |
| DS1 | Copper 8-144pairs | Tagged Only |
| DS3/STS1 | Coax (preferred 734C) | BNC Connector |
| Single Mode Fiber optic (All Others) | Single Mode Fiber Cable or Fiber Jumper | SC-UPC Connector |

The ILEC is responsible for thorough benchmark testing of all cabling and connectors from the CLEC Collocation Area back to the block/panel on the ILEC provided Frame. The Test and Acceptance testing should be recorded for subsequent benchmark comparisons with verifications of termination locations on the AT&T equipment side of the cable. Copies of the fiber acceptance test shall be retained by AT&T, and a copy shall be given to the CLEC. If the CLEC provides and installs the cable, no testing will be performed by AT&T.

The handoff point of cabling and connectors must be suitably labeled to facilitate the rapid installation of services by the CLEC's Supplier. Copper cable should be tagged by sheath typically in 50/100 pair complements. Coax cables should be tagged with transmit and receive leads individually tagged and the circuit pairs subsequently tagged together.

Fiber optic cable and/or jumpers will be tagged in sequential order by the termination count on the AT&T equipment panel count (e.g. 1-72 for a 72 port panel) some of the newer panels count 1-144 for a 144 port panel. Cable tags, with far-end termination details (e.g., shelf/bay/distribution frame block, circuit number, Transmit/Receive, etc.) shall be placed on the unterminated end of cables reserved for future use (by the Telco) or for collocation interconnection (by the CLEC). Note: If the cable is DSO cable for a CLEC, the cable tag needs to include what is stenciled at the MDF /IDF block. This tag will also include the CLEC cable name and Carrier Facility Assignment (CFA) information.

After CLEC acceptance of the ILEC provided interconnection cables, the standard ILEC test point for these new caged and cageless locations will be the last test point within the AT&T Equipment Area (e.g. MDF/IDF, DSX-1, DSX-3, FDF). Embedded services and pre-June 1999 Caged Collocation services will be handled in the previous test manner in their respective carrier areas.

ILEC Provided DC Power Cabling

For the DC power cabling, the demarcation point is either the CIPP (Collocation Interconnect Power Panel, if installed) or the coiled bare-ended cables. The ILEC Installation Supplier is obligated, by AT&T Installation Guidelines (TP 76300), to properly label (tag) and run the power cable from the source (either a BDFB or the power plant) to the agreed (assigned) location. Prior to job completion, continuity checks insure the cable is properly installed. Labeling at the source should identify the feeds as Collocation service, the engineered fuse size, and the exact location of the load (relay rack identification or Collocation cage number).

When bare-ended cables are provided to the CLEC, the cables shall be coiled, properly secured and tagged in the cable rack directly over or adjacent to the CLEC’s assigned space. Because the AT&T Installation Supplier generally completes the power installation prior to CLEC turnover, the ILEC Supplier shall label the cables with the CLEC ACNA (or CLEC name), Order Number, Feed Designation, Polarity and Number if necessary (i.e., Battery A1, Return A1, Battery A2, Return A2). The lettering shall be large and dark enough and arranged on the rack in such a way as to be visible from the floor. This allows the CLEC and AT&T LEC Representative to clearly identify the provisioned power feeds at the time of Collocation space acceptance and turnover. No joint test & acceptance (between the CLEC and AT&T LEC Power Installation Supplier) is necessary for job completion/space turnover. Any errors in labeling or other improper installation activities shall be noted at the ILEC to CLEC cage/space turnover.

Interoffice/Intraoffice Repeaters (IOR)  (ALL Regions)

One of the concerns when engineering the cabling between the Collocator’s equipment and AT&T's digital cross connect frame is cable distance and signal degradation. The following table provides the maximum cabling distance limitations for DS1 and DS3 circuits (without regeneration devices) using the ideal cable facilities.

DS1/DS3 Maximum Cable Limitations

| Type of Connection /Cable Used | Distance Limit (Network Element {NE}) -DSX1/DSX3) | Distance Limit Cross-Connect at DSX1/DSX3 | Maximum Overall Distance Limit (NE-NE)* |
| --- | --- | --- | --- |
| DS1 22 gauge wire | 612.5 feet | 85 feet | 1,310 feet |
| DS1 24 gauge wire | 507.5 feet | 85 feet | 1,100 feet |
| DS1 26 gauge wire | 407.5 feet | 85 feet | 900 feet |
| DS3 734C coax | 427.5 feet | 45 feet (standard cord) | 900 feet |
| DS3 734C coax | 427.5 feet | 88 feet (extended reach cord) | 943 feet |
| DS3 735C coax | 227.5 feet | 45 feet (standard cord) | 500 feet |
| DS3 735C coax | 227.5 feet | 88 feet (extended reach cord) | 543 feet |

* Notice that if a DS1/DS3 signal has portions of both types of cabling, the finer gauge value will need to be used.

In cases where this distance limit cannot be met to the CLEC from ILEC equipment, intraoffice repeaters may be used to regenerate the signal to meet service parameters for the circuit. If the transmission level meets the standards of service for the Interconnection DS1 or DS3 Handoff Point, but an intraoffice repeater is requested, it may be placed on the Collocator’s side of the POT or may be installed at any point within the CLEC’s equipment. This will be done at additional cost for the CLEC only when requested by the CLEC.

The need for regenerative devices such as the IOR will be a billable Custom Work Order item for requests that exceed the DSX-NE and/or Overall Distances. IOR placements will not be included in the established initial or augment timelines set forth for other equipment in any tariff or document unless it is specifically requested as a part of the initial Collocation Service request.

Collocators whose equipment is within the DSX distance limits will receive signals with levels below the DSX values, but still within the acceptable range for intra-office wiring. If AT&T is required to provide regeneration to compensate for loss values beyond the network point of termination, all costs to provide the regeneration will be billable to the Collocator, and the price will be developed as an ICB with payment required prior to the installation. (ICB’s are only available in the AT&T Southwest,  West and Midwest regions. In the Southeast region this would need and amendment to the contract.)

DSO/DSL/DS1 & DS3 Interconnection Cabling

DSO/DSL/DS1/DS3 Interconnection Arrangements will be provided as follows (AT&T Southwest, West and Midwest Regions:

Requests for DS0/DSL interconnection arrangements will be designed and installed in accordance to the Collocator's application and (Dependent upon applicable Tariff or ICA). Collocators may order DS0/DSL pairs in increments of 100 pairs specifying shielded or non-shielded cable. AT&T will install shielded or non-shielded cable as specified on the Collocator’s application for DS0 and/or DSL facilities from the Collocator’s Dedicated Space to the AT&T Main Distributing Frame. The Collocator will be responsible for terminating the cable in their equipment bay located within their Dedicated Space. At the Collocator’s request (dependent on tariff or ICA), AT&T will furnish and install interconnect blocks, which will be located within the Collocator's equipment bays in the location specified by the Collocator. If the Collocator elects to have AT&T provide the interconnect panels/blocks, AT&T will provide the panels/blocks specified in Appendix B of the CLEC Online web site, “AT&T Standard Interconnection Arrangement Termination Blocks & Panels”.   Requests for  DS1 and DS3 interconnection arrangements will be designed and installed in accordance to the Collocator's application and (Dependent upon applicable Tariff or ICA). AT&T will install the cable to the AT&T DSX1 and /or DSX3 facilities.

DSO/DSL/DS1/DS3  Interconnection Arrangements will be provided as follows: (AT&T Southeast Region)

Requests for DS0/DSL interconnection arrangements will be designed and installed in accordance to the Collocator's application and  Dependent upon applicable Tariff or ICA. Collocators may order DS0/DSL pairs per actual quantity ordered.  The CLEC will hire an  AT&T approved suppliers, eligible for the scope of work,   to perform the engineering and installation. AT&T will provide the path and racking the CLEC’s supplier will follow. The interconnect blocks will be supplied and owned by the CLEC.  Requests for  DS1 and DS3 interconnection arrangements will be designed and installed in accordance to the Collocator's application and (Dependent upon applicable Tariff or ICA .  The CLEC will hire an  AT&T approved suppliers, eligible for the scope of work,  to perform the engineering and installation.

Fiber Interconnection Arrangements  (ALL Regions) may be requested to interconnect with AT&T's fiber optic facilities or AT&T's Unbundled Network Elements (UNE’s). Fiber interconnection arrangements and the associated fiber panel are not used to terminate the Collocator’s fiber entrance cable. The Collocator must provide the fiber termination panel for its entrance cable as described in the Outside Plant Section of the Engineering section.

Fiber Interconnection Arrangements (AT&T Southwest,  West and Midwest Regions):

will be provisioned to the Collocator as follows:

(Dependent upon applicable Tariff or ICA) for each Collocator requesting fiber terminations, when AT&T is performing the installation, AT&T will provide fiber optic cable and/or jumpers terminated with SC-UPC connectors, tagged in sequential order by the termination count on the AT&T equipment panel counts. AT&T will provide jumpers or tagged fiber cable ends that the Collocator will terminate in their equipment bay within their Dedicated Space. At the Collocator’s request AT&T will provide a Fiber Interconnection panel which will be mounted in a location specified by the Collocator within one of the Collocators bays in it’s Dedicated Space.

Fiber Interconnection Arrangements (AT&T Southeast Region):

(Dependent upon applicable Tariff or ICA) Collocators may order Fiber interconnection arrangements.  The CLEC will hire an  AT&T approved suppliers, eligible for the scope of work,   to perform the engineering and installation. AT&T will provide the path and racking to the CLEC .

Collocator to Collocator Interconnection-  (AT&T Southwest, West and Midwest Regions)

(Dependent upon applicable Tariff or ICA)  AT&T will allow Collocators to interconnect its network with that of another Collocator in the AT&T's Eligible Structure if that Collocator is also using that equipment for interconnection to or access to UNEs. Within a contiguous area, AT&T shall permit a Collocator to connect its equipment with that of another collocated telecommunications carrier within the same Eligible Structure provided that the collocated equipment is also used for interconnection with AT&T or for access to AT&T's unbundled network elements. The Collocator will not be permitted to place cable over AT&T's switches or other critical equipment. AT&T will designate the space and supporting structures to be used for such facilities. AT&T shall permit Collocator to construct such facilities using copper or optical fiber facilities subject to the same reasonable safety requirements that AT&T imposes on its own equipment and facilities. All cable placed within the eligible structure must have a fire retardant (plenum rated) sheath. AT&T shall not require Collocators to purchase any equipment or cross-connect capabilities solely from AT&T itself at tariffed rates.

If the Collocators are not located in contiguous space and, therefore, cannot physically pull the cable themselves through the AT&T provided structure(s), AT&T will perform the necessary construction and perform the cable pull on a time and materials basis. At no time will Collocator be allowed access to any portion of the central office other than the collocation area — except for reasonable access to restrooms and parking lots where available. AT&T (1) will not make any physical connection within the Collocator’s dedicated space; (2) will not have any liability for the cable or the connections, or the traffic carried thereon; and (3) will not maintain any records concerning these connections.

Co-Carrier Cross Connect and Direct Cross Connection Arrangements-(AT&T Southeast Region)

General Information

(Dependent upon applicable Tariff or ICA)  AT&T will allow a Collocator to interconnect its network with that of another Collocator in the same AT&T Eligible Structure. AT&T will also allow a Collocator to connect to it's own bays.  The Collocator will not be permitted to place cable over AT&T's switches or other critical equipment AT&T will designate the supporting structures to be used for such interconnection cabling. AT&T shall permit the Collocator to construct such interconnect cabling using copper or optical fiber as specified in the collocation application subject to the same reasonable safety requirements that AT&T imposes on its own equipment and cabling.  All cable placed within the eligible structure must have a fire retardant (plenum rated) sheath. The CLEC will hire an  AT&T approved suppliers, eligible for the scope of work,   to perform the engineering and installation. AT&T will provide the path and racking to the CLEC .

Co-Carrier Cross Connection

In the Southeast region, AT&T shall permit a Collocator to connect its equipment with that of another   collocated telecommunications carrier within the same Eligible Structure. This type of arrangement is called Co-Carrier Cross Connection

Direct Cross Connection

In the Southeast region, Direct Cross Connection, connects two (2) non-contiguous arrangements owned by the same CLEC. The two arrangements can be anywhere within the Eligible Structure and could include connecting a cageless arrangement to a caged arrangement owned by the same CLEC.

CDOW  Section-(CLEC Doing Own Work)-- (AT&T Southwest, West and Midwest Regions only) CDOW Installation

CLEC should refer to the Installation section of this handbook. CDOW is dependant on ICA and state Tariffs. The CDOW option is only available in contracts in the 12 state region which includes AT&T-Southwest, AT&T West and AT&T Midwest.  In the AT&T Southeast 9 state region all contracts are written so that the CLEC must hire an AT&T approved suppliers, eligible for the scope of work,   to perform the installation.

Dependent on Tariff or ICA, the CLEC will specify their request to perform this CDOW function on their Collocation Application.

Function Collocator AT&T 1. Collocator Equipment Installation in Collocators designated space. Performs N/A 2. Installation of Cable Rack and Lighting or other Infrastructure for Cageless Collocation N/A Performs 3 Installation of Relay Rack/Bay for Virtual, Caged and Cageless Collocation Performs N/A 4. Walk-Through Meeting Requirement-Performs Performs 5. JSA/MOP Preparation Requirement-Performs N/A 5A Meeting with AT&T (GNFO-CO)/Collocator Personnel for discussion of Cabling & Terminations on AT&T Frames, BDFBs, and Power Boards Requirement-Performs Requirement-Perform by AT&T GNFO-CO 6. Validating Cable Path at walk through meeting Performs Provides Preliminary route 7. Copper Power and/or Switchboard and Fiber Cable Placement Performs N/A 8. Termination of Power Cable at BDFB (Includes Completion of BDFB Load Demand Worksheet) Performs N/A 9. Placement of fuse at BDFB Performs Performed by GNFO-CO if GNFO-CO deems necessary 10. Placement of Power Cable to Power plant Source (PBD) Performs N/A 10A. Termination of Power Cable at Power Board within 5 business days of Collocators request. N/A Performs 11. Placement of fuse at Power Board. N/A Performs 12. Cable Hole Fire Stop using AT&T approved methods for any cable holes opened during cable placement. NOTE: Does not include retrofitting cable holes to current standards. Performs N/A 13. Place New Cable Holes or Sleeves through floors/ceilings. Must be coordinated with Corporate Real Estate, GNFO-CO , and Floor Space Planner. N/A Performs Function Collocator AT&T 14. Assignment, Installation and Stenciling of AT&T Panels & Blocks on IDF or MDF. N/A Performs 15. Termination of cable on AT&T Panels & Blocks at AT&T assigned locations on AT&T Frames Performs unless this is prohibited by the Collocator's ICA or by State Tariff N/A 16. Continuity Testing from front side of Panel & Blocks to Collocator equipment through Collocator installed cable. Performs N/A 17. Running jumpers to Panels & Blocks (including Cross-Connects) as necessary to install, maintain, or disconnect service. N/A AT&T Personnel 18. Validating that Collocator cable has been placed to the correct location on the IDF or MDF as indicated by the AT&T stenciling/labeling on blocks. Performs N/A 19.BITS Timing Service Install and label BITS Timing Cable(s), Clock and all synchronization assignments. N/A Performs 20. Power Cable Removal Performs Performs if cable is abandoned by collocator & a valid trigger exists 21. BDFB Fuse Removal Performs Performs if fuse is abandoned by calculator or GNFO-CO deems necessary 22. Power Board/Panel Fuse Removal N/A Performs 23. Copper, Coaxial, and Fiber Cable Removals Performs Performs if cable is abandoned by Collocator & a valid trigger exist 24. Removal of Blocks on IDFs or MDFs N/A Performs 25. Removal of Collocator Owned Bays/Equipment Performs Performs if bay/equipment has been abandoned & a valid trigger exist 26. Removal of AT&T Owned Bays/Equipment N/A Performs *

CDOW - CLEC and ILEC Parallel Work - (AT&T Southwest, West and Midwest Regions only)

During the AT&T construction phase for Physical Collocation, if the ILEC engineering design work is complete (which includes asbestos removal, HVAC installation, filtration, floor loading, floor preparation and overhead racking & ironwork placement), AT&T will notify the Collocator that their Suppliers or contractors will be allowed to do work in parallel with AT&T throughout the remaining construction interval. This parallel work will only be allowed once an Initial Walk Through and the Space Turn-Over/Acceptance Meeting has taken place. This work will be allowed only if the CLEC has requested Parallel Work because of the CLEC critical completion dates.

Note: This parallel work by the CLEC's AT&T approved suppliers, eligible for the scope of work,   (Tier 1) can only be started after the Walk-Through Meeting, Job Start Agreement’s signing by AT&T GNFO-CO  and MOP signing by AT&T GNFO-CO  (if applicable). See sections on Walk-Through Meetings and MOPs for specific information. AT&T reserves the right to deny or halt any CLEC parallel work if such CLEC work creates a safety hazard to the AT&T Supplier or delays the completion of work by the AT&T Supplier. CLEC work would include the placement of equipment bays and cable. AT&T’s Supplier or Operating Turf Vendor (OTV)  for the central office will place or remove (where necessary) all infrastructure items.

Any parallel work done by the CLEC’s AT&T approved suppliers, eligible for the scope of work,   can be pulled for a AT&T “in-progress” quality audit.

CDOW - CLEC’s AT&T Approved Installation Supplier, eligible for the scope of work, Responsibilities -   (AT&T Southwest, West and Midwest Regions only)

ALL CABLE AND ROUTING STANDARDS  SHALL BE ADHERED TO DURING ALL ENGINEERING AND INSTALLATION ACTIVITIES.

The CLEC and/or the CLEC’s AT&T approved suppliers, eligible for the scope of work, is responsible for advising and coordinating with either the AT&T IE/CSPM when deviating from the agreed upon installation procedures/termination locations outlined in the Walk-Through Meeting or in the Space Turnover/Acceptance Meeting.

The CLEC’s AT&T approved suppliers, eligible for the scope of work,   will NOT store cable slack in excess of what is permitted in the AT&T TP76300 on any cable rack.

CDOW-Cabling Requirements

AT&T Cabling Standards & Routing

Standards

The CLEC’s AT&T approved suppliers, eligible for the scope of work, will be required to use fire-retardant cabling in the AT&T Central Offices and adhere to all applicable operations & Network Planning & Engineering (NP&E) documentation as follows:

- TP 76200 – Network Equipment – Building Systems (NEBS)

- TP 76300 – Installation Guide within the Central Office

- TP 76400 – Detail Engineer Requirements for the Central Office

- TP 76900– Installation Testing Requirements for the Central Office

- BSP 800-003-150, Cable & Wire Installation and Removal Requirements for Cable Racks and Raceways

- Interconnection Handbooks will reference these above listed documents for sources.

The AT&T Operating Turf Vendor (OTV) working with the ILEC Network Operations and the ILEC’s appropriate  IE will specify the route of ingress/egress for CLEC provided Cabling within an AT&T Central Office. The CLEC's AT&T approved suppliers, eligible for the scope of work, will be obligated to follow the instructions and route as specified during the Walk-Through Meeting. Cable routing information will be placed in the MOP by the CLEC’s.

The AT&T Operating Turf Vendor (OTV) working with the ILEC Network Operations and the ILEC Engineering Group will specify the route of ingress/egress for CLEC provided Cabling within an AT&T Central Office. The CLEC's AT&T approved suppliers, eligible for the scope of work, will be obligated to follow the instructions and route as specified during the Walk-Through Meeting. Cable routing information will be placed in the MOP by the CLEC’s AT&T approved suppliers, eligible for the scope of work, and will be required to place cable in accordance with the MOP. AT&T is not obligated or required to provide the CLEC or their authorized AT&T approved suppliers, eligible for the scope of work, a cable rack drawing for cable placement either during the Initial Walk Through Meetings or any additional meetings including the Space Turn Over/Acceptance Meeting.

CDOW- CLEC to CLEC Cable Routing

Any time a CLEC places additional equipment within their existing equipment bays, residing in a Physical Cageless Collocation Arrangement resulting in additional inter-bay cabling, an Augment request must be submitted by the CLEC. In a Physical Cageless Collocation Arrangement, the CLEC may cable between one piece of contiguous equipment to another in the same lineup in either of the two following methods

Note: Contiguous arrangements are equipment bays placed next to each other and having lineup contact within one lineup. This means that the bays are not separated by an aisle or pathway.

- The CLEC may elect to use the existing ILEC infrastructure Cable Racking and place their cable in existing rack if space is available or in proposed ILEC owned cable rack if space is not available. AT&T will not place cable racking dedicated to a specific CLEC. The CLEC will be billed for any cable placed on ILEC rack, either for CLEC ILEC connections or used to connect equipment shelves within the CLEC’s footprint, on a per cable sheath basis.

- The CLEC may elect to install their own cable racking directly above their equipment bay and within the CLEC’s assigned footprint, but below 7'6” in height. (Above this height, the ILEC racking will be placed only.) This CLEC racking will be placed in such a manner as not to interfere with existing or proposed ILEC lighting, fiber troughing, or egress/ingress in front or rear aisles, or present a safety hazard. The CLEC’s cable racking will be totally supported by the CLEC’s bays and be totally contained within the CLEC’s bay footprint. This CLEC cable racking placement shall be discussed and approved by the ILEC Engineer during the Walk-Through meeting.

Any time the CLEC places additional equipment within their existing equipment bays, residing in a Physical Caged Collocation Arrangement, any additional racking is the responsibility of the CLEC. However, this proposed CLEC cable racking shall be placed below an 8-foot height from the floor, and be totally within the area bounded by the CLEC’s cage walls. Such CLEC racking will NOT be supported by any ILEC ironwork (superstructure).

CDOW - Initial Walk-Through Meeting

The Walk-Through Meeting will establish the routes for all CLEC cable placements, the approximate location of CLEC’s cable terminations, fuse placements, as well as transportation and proper storage of materials during cable placement activities.

For cable removal activities, the Walk-Through Meeting will establish restrictions on removal routes, as well as validate locations of blocks on the IDF/MDF, panels and CLEC circuits within existing ILEC owned DSX1, DSX3, DCS1, DCS3, and FOT bays, and BDFB or Power Board terminations of CLEC power cable. Fusing at BDFBs and Power Boards will be discussed and ownership of these duties decided based on state CDOW tariffs, ICAs, or ICBs rules/agreements. Prior to any Walk-Through Meeting involving CLEC cable removals, the Collocation Services Account Manager must have in their possession a letter from the CLEC stating that all service on specific cable facilities to be removed has been disconnected.

The Walk Through Meeting will take place after the CLEC acceptance of the proposed placement or removal work, however, the exact number of calendar days after acceptance is an interval dictated by state CDOW tariffs, ICAs, or a mutually agreed upon interval between the CLEC and the AT&T CLEC Account Manager and Common System Project Manager (CSPM) personnel .

During the Walk-Through Meeting, the CLEC/CLEC’s AT&T approved suppliers, eligible for the scope of work, will be informed that any work done by the CLEC/CLEC’s AT&T approved suppliers, eligible for the scope of work,   is available to be pulled for quality by AT&T personnel or AT&T quality Suppliers.

The CLEC/ CLEC’s AT&T approved suppliers, eligible for the scope of work,   must provide a CLEC Work Order number that will be given to the AT&T quality personnel for inclusion in their routine quality audit job lists. This quality check will include compliance with the TP76300 and TP76400 and is the same quality check that is performed on AT&T cable placement jobs. Also, at any point during the CLEC’s Cable Placement job, any AT&T personnel, the Operating Turf Vendor (OTV) or any ILEC Supplier can request this quality audit. This in-progress quality check can also done on AT&T cable placement jobs.

If quality defects are found during the job, then AT&T Engineer should be notified by the AT&T quality auditor, and CSPM will notify the CLEC via email that the CLEC’s AT&T approved suppliers, eligible for the scope of work, has 5 working days to correct quality defects, then notify CSPM, who will call the AT&T quality auditor for a re-check. If quality defects are not corrected, then these defects will be noted in writing at the Space Turnover Meeting and all defects must be corrected by the CLEC’s AT&T approved suppliers, eligible for the scope of work, within 5 days after Space Turnover Meeting.

Continuity testing in accordance with TP 76900 – Installation Testing Requirements for the Central Office is not offered with CLEC Cable Placement. Additional testing using continuity, streaking or high stress testing through CLEC equipment is also not provided for under cooperative testing or this practice. Special requests for ILEC Supplier testing through CLEC equipment will be handled as a billable, independent activity regardless of the CLEC’s in-progress installation job time frame.

Walkthrough Meeting for new CLEC Cable Placements

This will be coordinated by the CSPM personnel and should include the following personnel from the ILEC and CLEC:

• Network Engineer (IE) or designated Engineering Representative

• Operating Turf Vendor (OTV)

• Network Operations (Central Office Management/GNFO-CO)

• CLEC Supplier (AT&T Approved supplier,eligible for the scope of work

• OSP Engineer and the OSP Planning Engineer (if appropriate)

The minimum requirements for termination location information to be given to the CLEC by AT&T’s IE at the Walk-Through are the following: The IE is responsible for providing frame (MDF or IDF) within 10 verticals and from Level A (Bottom) to the top of the frame of the final assignment by the AT&T Frame Planner, and AT&T personnel at the walk-through will determine the location of the BDFB where power cable will be terminated. DSX-1, DSX-3 and Fiber panel/termination locations will be determined within 25 cable feet of final bay locations. The confirmation of receipt of this termination information by the CLEC will be confirmed in writing to the IE either through a handoff at the Walk-Through Meeting, or an email from the CLEC to the IE following the Walk-Through Meeting.

The CLEC’s AT&T approved suppliers, eligible for the scope of work,  , IE, Operating Turf Vendor (OTV) (if applicable), GFNO-CO and the Space Planner (if in attendance), will determine the most optimum and least sensitive cable routes for placement of the all cables once the estimated cable termination locations are determined by AT&T, and given verbally to the CLEC and/or the CLEC’s AT&T approved suppliers, eligible for the scope of work, at the walk-through meeting. The IE gives estimated cable lengths to the CLEC or the CLEC’s AT&T approved suppliers, eligible for the scope of work,   after the cable route is determined by the AT&T IE. The CLEC should be told by the IE that the cable lengths are estimated cable lengths only, and that space on the cable racks will be available to ALL CLECs in parity on a “first come, first served” basis. AT&T will not be responsible for any overages or underages of cable due to changes in the cable route during actual cable placement. If there are discrepancies, it is the responsibility of the CLEC to resolve these through the IE. Any changes of termination requests by the CLEC will also void the agreed upon route and trigger another walk-through meeting. No guarantees on cable routing shall be given to the CLEC at any time during the Walk-Through Meeting.

- During the Walk Through Meeting, the ILEC’s representatives will walk the cable path and the CLEC’s AT&T approved suppliers, eligible for the scope of work, must take notes and measurements. After the walkthrough, the ILEC will send the CLEC estimated cable run lengths that can be used by the CLEC's Supplier to validate their own measurements. All information given to the CLEC will be marked as "estimated" and the CLEC must understand that any routes and terminations are not final until the Space Turn-over/Acceptance.

- If existing cable racking pile up exceeds 80%, necessitating a cable rack growth TEO issuance, then the IE will issue a separate job for infrastructure relief which will be coordinated with the CLEC’s cable placement job through the CLEC’s AT&T approved suppliers, eligible for the scope of work.  This cable rack exhaust will generally be noted before the Walk-Through Meeting and the IE will issue the cable rack relief job prior to the Walk -Through Meeting. CLEC Cable placement through cable holes should be noted on the walk-through--This cable hole/sleeve placement work shall be treated as parallel work.

- The physical placement of fuses at the BDFBs and Power Boards will be discussed and ownership of these duties decided based on state CDOW tariffs, ICAs, or ICBs rules/agreements.

Walkthrough Meeting for CLEC Cable Removals

The GNFO and/or Engineer reserves the right to determine how much, if any, cable the Collocators AT&T-12STATE Tier 1 Approved  Supplier,  eligible for the scope of work,  is allowed to remove.

This meeting will be coordinated by the   Common System Project Manager (CSPM)  and should include the following personnel from the ILEC and CLEC:

• Network Engineer (IE) or designated Engineering Representative

• Operating Turf Vendor (OTV)

• Network Operations (Central Office Management/GNFO-CO)

• CLEC Supplier (ILEC AT&T  (eligible for the scope of work) .

• COLD Engineer for the central office (unless full documentation for frame terminations have been given to the IE)

• OSP Engineer and the OSP Planning Engineer (if appropriate)

• This Meeting will take place only after approval by AT&T and the CLEC’s Account Representative to ensure that the CLEC’s request is legal and the meeting will not violate either the CLEC’s or AT&T’s rights.

• The CLEC AT&T approved suppliers, eligible for the scope of work, will adhere to all sections of the Network Facilities Cable Mining Guidelines and Requirements (BSP 800-003-200) and the TP76305 utilizing the most current version of the BSP and TP.

- Access to cable racks for tracing of cable to be removed.

- Removal of cable over areas in the Central Office that the GNFO or the IE deems sensitive will be not be performed.

- The ILEC GNFO reserves the right to schedule all cable removals during the maintenance window.

- Discussion of the exact method of removing material from the central office: this will include the use of Gaylord type boxes (large cable scrap tubs), selection of box removal paths through the central office, storage of the removed material outside the central office at the end of each removal shift, and the mechanism of the pick up of the material from the central office. AT&T’s GNFO reserves the right to limit the length of storage of removed material in the office. AT&T assumes no liability or financial responsibility for the removed material, and AT&T personnel will not sign any document associated with the pick-up and removal of the CLEC’s material from the central office.

- Cable owned by the ILEC remains the property of the ILEC even after the cable has been removed from the cable racks by the CLEC’s AT&T approved suppliers, eligible for the scope of work.  All ILEC owned cable will be turned over to the ILEC via an MDR for handling and capital recovery. All such removed cable shall be cut up into lengths of less than 4 linear feet and placed within suitable boxes (such as a Gaylord type box) which can be removed by hand jack from the removal area without any danger of service interruptions. The storage of such removed cable in boxes shall be coordinated with both GNFO and the IE as to ensure adequate and safe storage areas during removal operations.

- If the CLEC opts to abandon cable in place, in lieu of mining cable, then such abandonment, as well as, the CLEC’s giving up all future salvage rights to this cable, shall be provided in writing to the CLEC’s AT&T Account Manager, who shall in turn distribute to CSPM and the IE. All cable cut off and abandoned in place by the CLEC’s AT&T approved suppliers, eligible for the scope of work,   shall be tagged by this Supplier as “Abandoned In Place” and the CLEC’s ACNA stenciled on the cable tag.

- All fuses shall be properly identified on both ends, the fuse identified and pulled, prior to cutting any power cable serving CLEC power equipment.

Physical Entrance Facilities- General

(All Regions) -The Collocator must have a signed and approved Appendix to their ICA for Microwave Entrance Facilities before an application for Microwave Entrance Facilities can be issued

(All Regions) -The Collocator must contact the AT&T Towers Antenna Solutions Group at   www.atttowers.com before creating a Collocation Application in the AT&T Common Tool For Space (ACT) system.

Physical Entrance Facilities- AT&T-Southwest, AT&T West and AT&T Midwest

The Cable Entrance Facilities for caged, shared, or cageless applications are detailed below. At AT&T's discretion, conduit and/or dedicated cable racking will be provided from the first manhole to the Collocator’s Dedicated Space. The Collocator shall use a dielectric and fire retardant OFNR cable that has a sheath of either yellow or black with yellow strip, (plenum rated cables are used only where air handling systems are employed) as the transmission medium to the Dedicated Space or, where technically and structurally feasible, may use microwave. Collocation requests utilizing facilities other than fiber will be provided as an ICB. AT&T will only permit copper or coaxial cable as the transmission medium where the Collocator can demonstrate to AT&T that use of such cable will not impair AT&T's ability to service its own customers or subsequent Collocators.

Dielectric optical fiber cables manufactured for outside plant applications have flammable polyethylene sheaths. All cables used in equipment areas must meet Level 1 requirements as outlined in TP76200. Therefore, to meet fire resistance requirements the Collocator must provide dielectric fiber optic cable with a fire retardant sheath, (plenum rated cables are used only where air handling systems are employed).

If the Collocator provided dielectric fiber optic cable does not have a fire retardant sheath, to meet fire resistance requirements for bringing polyethylene sheathed fiber cables into equipment areas, a metallic conduit will have to be installed from the cable vault to the collocation area. Refer to TP76200.

Collocator employees, agents and contractors will be permitted to have access to the Collocator's cable only at the physical collocation space (where the cable is exposed for such access and where connections exist or are planned) and outside the entrance manhole (where the cable is delivered to AT&T). Access at any other location within the central office, cable vault, or within the conduit will not be permitted or required.

In order for AT&T to identify the entrance manhole(s) for the Collocator, the direction from which the cable(s) originate must be specified by the Collocator. AT&T will verify that a vacant access sleeve(s) or riser duct(s) exists at the entrance manhole(s). If none exists, construction of one will be required. If a vacant access sleeve or riser duct does not exist and one has to be constructed solely for the Collocator, the Collocator will pay for the construction on an Outside Plant Custom Work Order basis.

The Collocator will be provided with the total length requirements for the unbroken dielectric cable(s) that it must furnish to extend from outside the entrance manhole through the designated path and into the dedicated space. Measurement by AT&T will be made of the route into the entrance manhole from the delivery point, through that manhole, the vault, the conduit and/or cable racking and into the Collocator's Dedicated Space. This information will be provided to the Collocator and documented on the "Physical Collocation Application".

The Collocator will leave sufficient cable length outside the entrance manhole to allow AT&T to fully extend that cable from outside the entrance manhole, into and through that manhole, into and through the vault and into the Collocator’s dedicated space. Any excess cable will be brought into the Collocator's dedicated space and left as slack for the Collocator to install to its equipment.

On the "Outside Plant Field Survey" portion of the "Physical Collocation Application",  AT&T will provide to the identified Collocator contact (name and telephone number), the number of feet of cable required, the date the information was provided to the Collocator contact, and the name of the AT&T Engineer who provided it.

Diversity

Eligible Structure in which the Dedicated Space is located wherever there are at least two entry points for AT&T cable. AT&T will also provide nondiscriminatory access to any entry point into Eligible Structures in excess of two points in those locations where AT&T also has access to more than two such entry points. Where such dual points of entry are not immediately available, AT&T shall perform work as is necessary to make available such separate points of entry for the Collocator at the same time that it makes such separate points of entry available for itself. In each instance where AT&T performs such work in order to accommodate its own needs and those specified by the Collocator in the Collocator’s written request, the Collocator and AT&T shall share the ICB costs incurred by pro-rating those costs using the number of cables to be placed in the entry point by both AT&T and the Collocator(s) in the first twelve (12) months.

Note: On the Outside Plant Field Survey portion of the "Physical Collocation Application", the Collocator will identify its desire for "diverse entry" by checking "yes" on the form. In those offices where only one point of entry is used for AT&T's facilities, AT&T will keep a record of the Collocator's desire for alternate entry. Should AT&T provide another entry for its use, the Collocator will be notified that diversity at the office is available.

Any request for conduit usage, other than the entrance conduit, will be governed by current conduit leasing/licensing policies and pricing.

Physical Entrance Facilities- AT&T- Southeast.

Fiber Entrance Facilities are processed the same in the 9 State Southeast region be it a Physical or Virtual arrangement.

In both Physical and Virtual arrangements the Collocator is required to place fiber optic cable up to an AT&T Southeast- designated manhole, usually the last manhole prior to entering the CO vault.

AT&T Southeast will provide inner duct to facilitate placement of the cable, if desired by the Collocator. AT&T Southeast will install the fiber optic cable provided by the Collocator from the zero manhole to the vault and will make the cable splice at the vault (Refer to section (5) Attachment A).

The splicing methodology (i.e. mechanical, fusion, etc.) will be determined at the sole discretion of AT&T Southeast and comply with current AT&T standards. Additionally, all splicing peripherals, such as splice cases and splicing tools are also the responsibility of AT&T Southeast unless unique tools or testing equipment are required by the Collocator. In this event the Collocator is responsible for providing the desired tools and equipment.

No splice is allowed in the zero manhole, however, a splice is required at the CO vault. Therefore, the Collocator is required to leave enough cable slack to allow for placement from the zero manhole to the CO vault. Exception to the splice in the vault: If the Collocators Fiber Entrance cable is Dielectric Fire Retardant cable, NO splice will be needed.

For the purpose of interconnection, the duct facilities extended from the interconnect manhole to the central office vault are specific to the Collocator. Therefore, no other Collocator's cable, or AT&T Southeast cable is allowed in the same physical duct occupied by a Collocator. If multiple Collocator's are present in a central office, each must have a separate duct entrance into the vault.

For smaller central offices that do not have vaults, the demarcation point will be determined at the discretion of the Outside Plant Engineer for buried applications, or should be the top of the last pole entering the CO for aerial applications.

The Collocator is solely responsible for providing the fiber optic facilities to the zero manhole, including such duties as acquiring city, county, or state permits, inspections, complying with environmental regulations, etc.

The Collocator must work closely with the AT&T Southeast C&E Outside Plant DBT Engineer to ensure that the fiber optic cable entrance facilities are of the proper length and type. All fiber optic cable placed from the zero manhole to the CO vault will comply with AT&T corporate Standards.

As information, the Collocator’s AT&T Approved Installation Supplier (AIS) will work closely with network personnel to determine riser cable path. The AIS will do appropriate engineering to determine proper length and insure the cable meets all TP requirements. This would also apply if entrance cable requiring no splice is being used instead of riser cable.

The Collocator is not allowed to create physical entry points into manholes such as core boring into the manhole wall to place cable knockouts, lateral duct, etc. In the event that facilities are not available for manhole entry, AT&T Southeast or its designated contractor will perform the necessary make -ready work ahead of the Collocator's planned manhole entry. The cost associated with this work is averaged into the cable installation fee charged to the Collocator. In general, all expenditures for standard Collocator make-ready work and fiber cable installation/splicing are recovered via the cable installation fee. Therefore, unless special circumstances are present, the OSP work required for Collocation should be classified as routine, steady-state operations.

Vault to Collocator's Arrangement

It is recommended that the Collocator utilize pre-terminated dielectric, fire retardant cable to be placed by the Collocator’s AT&T Approved Installation Supplier, eligible for the scope of work, from the vault splice to the designated central office collocation arrangement. It is recommended that the riser cable be pre-terminated on a fiber optic splicing shelf utilizing SC connectors for ease of installation by the AIS. All riser cable must meet the specifications outlined in the AT&T Technical Publications. The Collocator is responsible for hiring an AT&T Approved Installation Supplier, eligible for the scope of work, for the placement and maintenance of this cable. Should the Collocator desire, instead of using pre-terminated fiber at the collocation arrangement, that the splice be made by the installation supplier, the Collocator must ensure that the installation supplier is certified to perform fiber optic splicing.

AT&T's Outside Plant Construction forces will also perform a fiber optic OTDR test, as indicated on the EWO, in the vault. The purpose of the OTDR is to test for fiber continuity and integrity at central office vault splice only. Additional splicing requirements and or changes to the existing arrangement will be handled via special construction in accordance with the existing tariffs.

Diversity

Eligible Structure in which the Dedicated Space is located wherever there are at least two entry points for AT&T cable. AT&T will also provide nondiscriminatory access to any entry point into Eligible Structures in excess of two points in those locations where AT&T also has access to more than two such entry points. Where such dual points of entry are not immediately available, AT&T shall perform work as is necessary to make available such separate points of entry for the Collocator at the same time that it makes such separate points of entry available for itself. In each instance where AT&T performs such work in order to accommodate its own needs and those specified by the Collocator in the Collocator’s written request, the Collocator and AT&T shall share the ICB costs incurred by pro-rating those costs using the number of cables to be placed in the entry point by both AT&T and the Collocator(s) in the first twelve (12) months.

Note: On the Outside Plant Field Survey portion of the "Physical Collocation Application", the Collocator will identify its desire for "diverse entry" by checking "yes" on the form. In those offices where only one point of entry is used for AT&T's facilities, AT&T will keep a record of the Collocator's desire for alternate entry. Should AT&T provide another entry for its use, the Collocator will be notified that diversity at the office is available.

Any request for conduit usage, other than the entrance conduit, will be governed by current conduit leasing/licensing policies and pricing.

# Text boxes

This document currently covers the following AT&T Local Exchange Carriers

AT&T-Southwest (Texas, Missouri, Oklahoma, Kansas, and Arkansas)

AT&T-West (California and Nevada)

AT&T-Midwest (Ohio, Wisconsin, Illinois, Michigan and Indiana)

AT&T- Southeast (Alabama, Florida, Georgia, Kentucky, Louisiana, Mississippi, North Carolina, South Carolina, Tennessee)

Note: This document covers all regions, unless specified in individual paragraphs that the process is region specific.

NOTE:  Information supplied in this Handbook is for informational purposes only.  For detailed and contractual information please refer to your current contract with AT&T such as ICA’s, Tariffs or other legally binding contracts in your specific region.  All such contracts take precedent over information supplied in this handbook document.

The Fiber Optic Raceway/Ductwork may be placed either prior to or at a later time when CLEC requests for Fiber jumper interconnection are made. Fiber downspouts will be placed only to the specified bay when a CLEC orders fiber interconnection with the AT&T network at a bay location.   Refer to AT&T Standards and Drawings for all ordering information.

IMPORTANT:

When reading the chart below the installation of cable will be determined by two factors: (1) the ICA and Tariff and (2) the region  that the CLEC is requesting service.

Standard power increments are dependent on State Tariffs, ICA's or MOU's in the all regions.

The CIPP is required for CLEC requests greater than 50 amps

The CIPP is CLEC provided dependant upon State Tariff or ICA.  The CLEC’s supplier can order directly from PECO II and will need to provide PECO II with a PO# and CLLI code.

The CLEC’s supplier should refer to Drawing ATT-P-05911-E for PECO II ordering information

Or

The panel can be order from Trimm Inc. 407 Railroad St Butner, NC 27509. 1-800-298-7466 Ricky Brummitt or Will Newton ordering information is TRIMM Collocation Interface Power panel (CIPP panel) - part #937200111 - OIN # ATT.PWPYADARRA - PAN 2013-003.

NOTE:  Information supplied in this section is for informational purposes only.  For detailed and contractual information please refer to your current contract with AT&T such as ICA, Tariff or other legally binding contracts in your specific region.  All such contracts take precedent over information supplied in this section.

Application Section – Interconnection Requirements (Dependent upon applicable Tariff or ICA authorization). The Collocator is to indicate the quantity of interconnection requirements needed on their application (Note: Ordering increments by applicable Tariff or ICA Authorization).

AT&T Southwest, West and Midwest region per Tariff and ICA only.

AT&T Southeast region the CLEC must hire an Approved Installation Supplier, eligible for the scope of work, to perform all CLEC installation and testing work functions.

The CLEC’s Approved Supplier is to follow all AT&T standards and drawings

The functions in the following table will become the respective responsibilities of the parties involved when the Collocator elects to employ an appropriately qualified AT&T Approved Tier 1/Tier2 Supplier (eligible for the scope of work)  WITH NO EXCEPTIONS.

Cable Ownership:

• AT&T ILEC provided cable is owned by ILEC--the designated Demarc is the end of the cable handed to CLEC

• CLEC provided cable is owned by CLEC--the designated Demarc is the ILEC owned Demarc panel/block .

CDOW Installation.

CLEC should refer to the Installation section of this handbook. CDOW is dependant on ICA and state Tariffs. The CDOW option is only available in contracts in the 12 state region which includes AT&T-Southwest, AT&T West and AT&T Midwest.  In the AT&T Southeast 9 state region all contracts are written so that the CLEC must hire an AT&T approved suppliers, eligible for the scope of work to perform the installation.