SBC - Building Requirements for GigaMAN and FibreMAN

This document will assist SBC customers with installations of GigaMAN® and FibreMANsm service.   While SBC attempts to meet customer requirements when installing service, these standards are required to ensure that customers purchasing these services encounter no service-related problems or outages, as a result of non-standard implementation practices.

GigaMAN and FibreMAN equipment have footprints and floor space requirements similar to other optical transport equipment.   Higher bandwidth equipment (for multiple circuits) may require more than one bay or cabinet and different power requirements.   A sample diagram of the equipment requirements is included at the end of this document.   An SBC engineering representative will clarify if any variations are necessary once the type of equipment is determined.

SBC Sales Teams are required to review this document with customers during the sales process.

This document, with SBC account rep signature, should then be submitted with the customer’s firm order.

*** The requirements outlined below are the responsibility of the customer ordering service. ***

Single Point of Contact (SPOC) –  Customers ordering service from SBC must provide a local contact’s name and phone number with whom the SBC engineering representative can speak regarding scheduling, building access and problem resolution, should the need arise.  A site visit by SBC engineering personnel will be scheduled with a customer single point of contact (SPOC) post-sale, unless a pre-sales visit is deemed necessary by SBC.  In order for SBC to provide a firm provisioning interval during the site visit, the SPOC must:

- Be familiar with the location where service has been requested

- Have decision making authority to address the service requirements requested

- Have the authority to commit to a “ready date” for all requirements that are the responsibility of the customer

Note: For resale orders, the Reseller ordering from SBC, and not the end-user, is responsible for coordinating and meeting the customer requirements listed herein.

Fiber Cable Supporting Structure – A clear underground or aerial path is required from the property line where SBC facilities exist, to the (telephone) equipment room to support the entrance fiber.  For example, if conduit is used:

- Minimum 2” conduit with a pull rope from the property line to the point of entrance. A 4” conduit is recommended, and 4” conduit – schedule 40 is required in some regions (e.g. SBC East and SBC West for new constructions).

- Minimum 3’ sweeping radius – no right angles – no more than three 90˚ angles without a pull box.  Dimensions required for pull box space are 12” x 12” x 18”.

- A clear path with conduit or cable tray needs to be provided from the point of entrance to the demarcation location where the equipment will be placed (if applicable).

- Customers are encouraged to share this information with their Electrical Contractor.

# Floor Space and Environmental Requirements

# As a standard, fiber transport equipment is placed in a common area with access to the entire building.  It is the tenant’s responsibility to obtain the necessary permissions from the building owner for use of the common area.  Equipment may be placed in a customer suite if multiple individual demarcs have been established for the specific building.  SBC 13-state demarc policy must be followed in all cases.

- Please see the drawing on page 6 for the minimum space requirements for GigaMAN equipment.  In addition to the space reflected on this drawing, we also require a clear 3’ area around the equipment for access.  Specific requirements may be discussed with the SBC engineering representative.

- Rack Mounted Installations can be placed only in a secured customer telecommunications closet or room.  The standard for rack mount is an entire 23" wide, seven-foot bay, as depicted in the drawing below.  As an alternative, EIA Standard 19” wide, seven-foot bays are also approved for use. The equipment will be delivered with its own rack provided by SBC.  SBC equipment is not normally placed in any customer provided racks or cabinets (see note # 4).  Also, customer equipment cannot be placed in any SBC provided rack or cabinet.

- Cabinet Installations are available.  Cabinets will be provided by SBC per standard, approved configurations.  SBC equipment is not normally placed in any customer provided racks or cabinets (see note # 4).   Also, customer equipment cannot be placed in any SBC provided rack or cabinet.

- SBC provides a rack or cabinet as part of standard product deployment, and recommends this method as the standard provisioning arrangement.  If a customer scenario necessitates the consideration for a customer-provided rack or cabinet, the account team can request a non-standard, customer provided arrangement using the embedded form.  NOTE: the additional time to consider and approve the non-standard request will add to the overall interval.   Information on the form must be complete and submitted by the account team according to the instructions in the form.   Order cannot proceed until Customer Provided Rack or Cabinet Requests are approved by the SBC Network Staff.

(Click on the icon above to open the Request for Customer Provided Rack form)

- SBC will normally provide a rack or cabinet dedicated to GigaMAN/FibreMAN equipment and recommends this method as the standard provisioning arrangement.  If a customer scenario necessitates the consideration of locating SBC network equipment associated with different types of services (e.g. SONET and GigaMAN) in the same rack/cabinet, the account team can request approval for Non-Standard Deployment, Mixed SBC Services, using the embedded form.  Customer should be aware that such arrangements may limit growth capacity for either service, and may result in future costs to rearrange service or equipment to support such growth.  NOTE: the additional time to consider and approve the non-standard request will add to the overall interval.   Information on the form must be complete and submitted by the account team according to the instructions in the form.   Order cannot proceed until the Mixed Services request is approved by the SBC Network Staff.

(Click on the icon above to open the Request for Mixed SBC Network Services Equipment form)

- The floor must be sturdy and able to withstand from 750 lbs. (without batteries) to 1,100 lbs. (with batteries) per bay of equipment.

- Operating environment should be between +40˚ F and 100˚ F at 20% to 50% relative humidity.

- With cabinet installations, if the floor is a raised computer floor, there must be no obstructions below the floor tiles and a small section of tile must be cut to allow for cable entry.

- Other regional specifications must be met as dictated by OSHA and local regulatory agencies (e. g. Earthquake Bracing).

- Wall-Mounted Installations are also available.  The following provides general specifications for customer premises requirements associated with GigaMAN installations that will use the GigaMAN OM5100 AC Powered Customer Premise Wall-Mount Cabinet.  DC powered options are not available in the wall-mounted configuration.

A)  General information:

- Overall dimensions:  25.13 in. (H) X 25.93 in. (W) X 13.41 in. (D)

- Max loaded weight:  150 lbs.

- Max. AC current draw:  5.9 amps @ nominal 110V AC

- Cord provided:  One 10 ft. cord with 120V/15A twistlock plug for all applications.

AC outlet required:  NEMA L5-15R 110V/15A - Twistlock

B) Room information:

- Wall must allow approximately 3' x 3' for installation, minimum (4’ x 4’ is preferable to accommodate fiber distribution panels)  and must be at standing height.

- Customer must provide mounted backboard (3/4" plywood) attached to wall studs or cinderblock per industry practice, to support max loaded weight of 150 lbs, before cabinet is installed.  Customer must provide power supply; specifically, a single 110V, 15A AC outlet equipped with a NEMA L5-15R receptacle, which must be located close enough to the equipment that a 10 ft. cord will reach the outlet (see item A above).

- Customer must provide space to accommodate 2 fiber distribution panels; 1 for SBC fiber into building and 1 as a customer fiber demarcation point.

- Cabinet does not need to be in same room as fiber termination demarcation point, but should be within reach according to technical specs of fiber cross-connect cable, i.e. approximately 50'.

C) Caveats:

- This cabinet will support two protected (GigaMAN only) or four unprotected GigaMAN or FibreMAN circuits.

- The current model does not include a front cover.  Installations in 2004 will not include a front cover.  If a model with front cover is approved for use by SBC in 2005, installations after that approval date will have option of including a front cover.  SBC will not be retrofitting front covers on cabinets previously installed without covers.

- Power protection is not offered with wall mount applications. Customers can supply protection to the AC power source provided to SBC, but cannot locate the equipment in the SBC cabinet.  SBC has a power protection option for GigaMAN, but that option is only available with rack and cabinet installations.

# Power – It is required that the customer provide permanent dedicated power circuits for the equipment being installed.  GigaMAN/FibreMAN equipment is DC powered.  The customer power feed may be DC or AC, with one exception.  If a customer orders power protection, and a separate bay is required (see power protection notes), then the configurations supported by the bulk power assembly must be DC powered. Rectifiers are placed with the equipment for AC power feeds.  Power requirements vary by region, as specified below.   Note that the requirements below are for rack mounted configurations.  Wall-mounted requirements are listed under item 10 on pages 3-4 of this document.

West, Southwest, and East:

### 1)  Nortel 5100 shelves (maximum of 4 OM5100 shelves per 19” or 23” rack):

- If AC powered, customer must provide TWO NEMA L5-30R 110V/30A outlets on separate breakers.

- If DC powered, customer must provide TWO -48v DC power leads rated and fused at 30 amps each, with wiring brought to SBC relay rack.  The wiring will be provided by customer, and must meet local electrical standards.  SBC personnel will terminate wiring to fuse and alarm panel.

2)  Nortel 5200 shelves (maximum of 2 OM5200 shelves per 19” or 23” rack):

a)  If AC powered, customer must provide TWO NEMA L5-30R 110V/30A outlets.

b)  If DC powered, customer must provide TWO -48V DC powered leads rated and fused at 40 amps each.

Certain cabinet types may limit the number of shelves that can be deployed, but the power requirements are the same for both relay rack and cabinet installations.

Midwest:

### 1)  Nortel 5100 shelves in a standard 19” or 23” relay rack (maximum of 4 OM5100 shelves per rack):

a)  If AC powered, customer must provide ONE NEMA L6-30R 220V/30A outlet.

b)  If DC powered, customer must provide TWO -48V DC power leads rated and fused at 30 amps each.

2)  Nortel 5100 shelves in a standard SBC Midwest customer premise cabinet (maximum of 4 OM5100

shelves per cabinet):

a)  If AC powered, customer must provide ONE NEMA L6-30R 220V/30A outlet to power the rectifiers and ONE NEMA L5-20R 110V/20A outlet to power the fan unit at the top of the cabinet.

b)  If DC powered, customer must provide TWO -48V DC power leads fused at 30 amps each and ONE NEMA L5-20R 110V/20A outlet to power the fan unit at the top of the cabinet.

3)  Nortel 5200 in a standard 19” or 23” relay rack (maximum of 2 OM5200 shelves):

a)  If AC powered, customer must provide ONE NEMA L6-30R 220V/30A outlet.

b)  If DC powered, customer must provide TWO -48V DC powered leads rated and fused at 40 amps each

4)  Nortel 5200 in a standard SBC Midwest customer premise cabinet (maximum of 1 OM5200 shelf):

a)  If AC powered, customer must provide ONE NEMA L6-30R 220V/30A outlet to power the rectifiers and ONE NEMA L5-20R 110V/20A outlet to power the fan unit at the top of the cabinet.

b)  If DC powered, customer must provide TWO -48V DC power leads rated and fused at 30 amps each and ONE NEMA L5-20R 110/20A outlet to power the fan at the top of the cabinet.

# Power Protection (Battery Backup) service is now currently available with GigaMAN, if the customer orders it.  If power is lost and the customer has power protection, the batteries will provide 8 hours of back-up.

# Please NOTE:  Power protection for a bay with up to two 5100 shelves can be provided in the same bay as the GigaMAN/FibreMAN equipment.  Power protection for a bay with one or two 5200 shelves or more than two 5100 shelves will require a separate bulk power bay.  These bulk power bay assemblies require the customer to provide 2 AC outlets and floor space for an additional 7 ft. rack assembly with a footprint that is approx. 25 in. wide and 21 in. deep. The GigaMAN configurations supported by these bulk power assemblies must be DC powered (not AC). Power protection will be available for order against one circuit, but will protect all equipment/services in the rack, subject to the above limits.  In a multi-customer environment, the power protected rack will have to be exclusive to the power protection customer, which may require service rearrangement on existing services.

# Grounding – If the customer site will be using a stand-alone, centralized bulk power plant (now or at any time in the future), then grounding is required as follows:  #2 stranded ground is required from the customer's earth electrode system to the equipment room.  This would be connected to a grounding bus bar, or otherwise directly connected to different components.  A #6 stranded ground is required from the grounding bus bar to the GigaMAN network equipment.

If the customer site will not be using a stand-alone, centralized bulk power plant (now or at any time in the future), and instead will be using an embedded or integrated power configuration (where the power plant is located within the same rack or cabinet as the equipment it powers), then grounding is required as follows:  A #6 stranded ground is required from the customer's earth electrode system to the equipment room.  This would be connected to a grounding bus bar, or otherwise directly connected to different components.  A #6 stranded ground is required from the grounding bus bar to the GigaMAN network equipment.

# Support Structure – When equipment is to be placed in the center of a terminal room, overhead ladder racking or under floor cable tray from the wall to the fiber equipment must be provided

Client Dmarc panel - GigaMAN and FibreMAN are handed off via fiber jumpers that are terminated at a Fiber Distribution Frame cross connect at the demarc.  Typically, the demarc interconnection panel is in a separate bay or backboard location from the bay containing the GigaMAN/FibreMAN equipment.

# Wall Backboard – 4’ x 8’ x 3/4” Fire rated Plywood fastened to studs.    In some instances, at customer request, a customer provided bay can be used in lieu of the wall backboard.  This alternate arrangement must be discussed with the SBC engineering representative, and is only applicable to fiber distribution panels.  When using a wall-mounted configuration, it is possible that the wall backboard could be smaller than 4’ x 8’, but this will need to be discussed with an SBC engineering representative.

###### Account Manager: ______________________________________________________________

Telephone Number: ___________________________________________________________________

Date Covered with Customer:      /   /200    (Month/Day/Year)

Customer Site Contact Name: __________________________________________________________

Telephone Number: ___________________________________________________________________

- The equipment examples below depict minimum footprint requirements for GigaMAN and/or FibreMAN equipment systems with the approximate bandwidth capacity from 1 to 8 circuits.

Note:  If using the 19” EIA relay rack, minimum footprint is reduced from 27” across to approximately 23” across.  Other requirements are unchanged with the 19” EIA rack.

# Text boxes

Requires 1’ clearance on top for fan exhaust.

Requires 3’ clearance from power.

### 7 FT. RELAY RACK FOOTPRINT

7½”

10”

6½”

24”

27”

5100 bay

CABINET FOOTPRINT

84½” height

33½”

99”

32”

Requires 35” front to rear access

between line-ups.

Requires 1’ clearance on top for cabling.

Requires 3’ clearance from power.

Leave 8“ between bays when multiple bays

are required.

If using 19” EIA relay rack, measurement across bay is reduced to approximately 23”.

33½”

Door

Door

Front

Rear

33½”

Front

Top view looking down